## Index
INDEX | Technology Data for Energy storage
140 PTES seasonal | Version: | 9
141 Large hot water tank | All cost data is in | 2020 | EURO
142 Small scale hot water tank | License:
143a Rock-based Carnot battery | This work is licensed under Attribution 4.0 International
143b Molten salt Carnot battery
150 Underground Storage of Gas
151a Hydrogen Storage - Tanks
151b Hydrogen Storage - LOHC
151c Hydrogen Storage - Cavarns
160 Pumped hydro storage
161 CAES
162 Flywheels
180 Lithium Ion Battery
181 Vanadium Redox Flow Battery
182 Na-S Battery
183 Na-NiCl2 Battery
The data sheets are continuously updated as technologies evolve, if the data changes significantly or if errors are found. The date for the latest update is listed in the index below and also indicated in the specific datasheets.
INDEX:
all sheets, update to 2020 prices (added Aug 2023)
180 Chapters on LIB (added Jan 2019)
181, 182 and 183 Chapters on VRB, NaS and NaNiCl2 batteries (added Dec 2018)
180 Batteries NaS and VRB chapter (removed Dec 2018)
140 PTES (updated Oct 2018)
141 Large scale hot water tank (updated Oct 2018)
142 Small scale hot water tank (added Aug 2019)
150 Underground storage of gas (transferred from previous catalogue for el and DH from 2012 Oct 2018)
151 Hydrogen Storage (transferred from previous catalogue for el and DH from 2012 Oct 2018)
160 PHS (transferred from previous catalogue for el and DH from 2012 Oct 2018)
161 CAES (Updated Nov 2018)
180 Batteries NaS (transferred from previous catalogue for el and DH from 2012 Oct 2018)
180 Batteries VRB (transferred from previous catalogue for el and DH from 2012 Oct 2018)
140 PTES (updated Feb 2025)
143 Rock-based Carnot battery (added Feb 2025)
143 Molten Salt Carnot battery (added Feb 2025)

## alldata_flat
ws | Technology | cat | par | unit | priceyear | note | ref | est | year | val
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Lower | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Lower | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Upper | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Upper | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2025 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2030 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2035 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2040 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | Lower | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | Lower | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | Upper | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | Upper | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2025 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2030 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2035 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2040 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | - Discharge efficiency [%] | pct. |  | B |  | ctrl | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2025 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2035 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | Lower | 2020 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | Lower | 2050 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | Upper | 2020 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | Upper | 2050 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2020 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2025 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2030 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2035 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2040 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C | 5 | ctrl | 2050 | 0.02
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2020 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2050 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2020 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2050 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2025 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2030 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2035 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2040 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2050 | 2
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | Lower | 2020 | 0.04
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | Lower | 2050 | 0.04
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | Upper | 2020 | 0.1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | Upper | 2050 | 0.1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2020 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2025 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2030 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2035 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2040 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy losses during storage [K/day] | K/day |  | B | 12 | ctrl | 2050 | 0.08
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | Lower | 2020 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | Lower | 2050 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | Upper | 2020 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | Upper | 2050 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2020 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2025 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2030 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2035 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2040 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2050 | 4500
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2025 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2030 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2035 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2040 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2025 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2035 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Heat
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | Lower | 2020 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | Lower | 2050 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | Upper | 2020 | 150
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | Upper | 2050 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2020 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2025 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2030 | 150
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2035 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2040 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Input capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2050 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | Lower | 2020 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | Lower | 2050 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | Upper | 2020 | 150
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | Upper | 2050 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2020 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2025 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2030 | 150
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2035 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2040 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Output capacity for one unit [MW] | MW |  | A | 5 | ctrl | 2050 | 200
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | Lower | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | Lower | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | Upper | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | Upper | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2020 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2025 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2030 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2035 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2040 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2050 | 1
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | Lower | 2020 | 0.75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | Lower | 2050 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | Upper | 2020 | 0.9
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | Upper | 2050 | 0.95
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2020 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2025 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2030 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2035 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2040 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Round trip efficiency [%] | pct. |  | B, I | 1, 5, 14, 23 | ctrl | 2050 | 0.8
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | Lower | 2020 | 20
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | Lower | 2050 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | Upper | 2020 | 40
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | Upper | 2050 | 50
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2020 | 20
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2025 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2030 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2035 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2040 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Energy/technical data | Technical lifetime [years] | years |  | D | 24 | ctrl | 2050 | 30
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | Lower | 2020 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | Lower | 2050 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | Upper | 2020 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | Upper | 2050 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2020 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2025 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2030 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2035 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2040 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof equipment [%] | pct. |  |  | 5 | ctrl | 2050 | 75
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | Lower | 2020 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | Lower | 2050 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | Upper | 2020 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | Upper | 2050 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2020 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2025 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2030 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2035 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2040 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | - hereof installation [%] | pct. |  |  | 5 | ctrl | 2050 | 25
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | Lower | 2020 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | Lower | 2050 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | Upper | 2020 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | Upper | 2050 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2020 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2025 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2030 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2035 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2040 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Fixed O&M [M€/GWh Capacity/year] | MEUR/GWh/year | 2020 | G | [1, 5] | ctrl | 2050 | 2.5
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | Lower | 2020 | 0.90289
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | Lower | 2050 | 0.74356
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | Upper | 2020 | 1.2216
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | Upper | 2050 | 1.0622
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2020 | 1.0622
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2025 | 1.0622
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2030 | 1.0622
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2035 | 1.0622
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2040 | 0.98256
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Specific investment [M€/GWh Capacity] | MEUR/GWh | 2020 | F | 5 | ctrl | 2050 | 0.90289
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | Lower | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | Lower | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | Upper | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | Upper | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | ctrl | 2020 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | ctrl | 2025 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | ctrl | 2030 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | ctrl | 2040 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | G | [1, 5] | ctrl | 2050 | 0
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | Lower | 2020 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | Lower | 2050 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | Upper | 2020 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | Upper | 2050 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2020 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2025 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2030 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2035 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2040 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Max. storage temperature, hot [⁰C] | ⁰C |  |  |  | ctrl | 2050 | 90
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | Lower | 2020 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | Lower | 2050 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | Upper | 2020 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | Upper | 2050 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2020 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2025 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2030 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2035 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2040 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage medium |  |  |  |  | ctrl | 2050 | Water
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | Lower | 2020 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | Lower | 2050 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | Upper | 2020 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | Upper | 2050 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2020 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2025 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2030 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2035 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2040 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage temperature, discharged [⁰C] | ⁰C |  | H |  | ctrl | 2050 | 35
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | Lower | 2020 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | Lower | 2050 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | Upper | 2020 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | Upper | 2050 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2020 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2025 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2030 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2035 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2040 | 70000
140 PTES seasonal | Pit Thermal Energy Storage [PTES] | Technology-specific data | Storage volume for one unit [m3] | m3 |  |  |  | ctrl | 2050 | 70000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | Lower | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | Lower | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | Upper | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | Upper | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | ctrl | 2015 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | ctrl | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | ctrl | 2030 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | ctrl | 2040 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | C |  | ctrl | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2015 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2020 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2030 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2040 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2050 | 100
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | Lower | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | Lower | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | Upper | 2020 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | Upper | 2050 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | ctrl | 2015 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | ctrl | 2020 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | ctrl | 2030 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | ctrl | 2040 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | D | 7 | ctrl | 2050 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | Lower | 2020 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | Lower | 2050 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | Upper | 2020 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | Upper | 2050 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | ctrl | 2015 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | ctrl | 2020 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | ctrl | 2030 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | ctrl | 2040 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | G | 7 | ctrl | 2050 | 0.5
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | Lower | 2020 | 0.14286
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | Lower | 2050 | 0.14286
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | Upper | 2020 | 0.24286
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | Upper | 2050 | 0.24286
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | ctrl | 2015 | 0.18571
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | ctrl | 2020 | 0.18571
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | ctrl | 2030 | 0.18571
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | ctrl | 2040 | 0.18571
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  |  | 2 | ctrl | 2050 | 0.18571
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Lower | 2020 | 45
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Lower | 2050 | 45
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Upper | 2020 | 315
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Upper | 2050 | 315
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2015 | 175
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2020 | 175
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2030 | 175
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2040 | 175
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2050 | 175
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | Lower | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | Lower | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | Upper | 2020 | 3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | Upper | 2050 | 3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | ctrl | 2015 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | ctrl | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | ctrl | 2030 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | ctrl | 2040 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 7 | ctrl | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Heat
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | Lower | 2020 | 0.8
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | Lower | 2050 | 0.8
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | Upper | 2020 | 5.3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | Upper | 2050 | 5.3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2015 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2020 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2030 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2040 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2050 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | Lower | 2020 | 0.8
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | Lower | 2050 | 0.8
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | Upper | 2020 | 5.3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | Upper | 2050 | 5.3
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2015 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2020 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2030 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2040 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [MW] | MW |  | B | 7 | ctrl | 2050 | 2.9
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | Lower | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | Lower | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | Upper | 2020 | 4
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | Upper | 2050 | 4
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | ctrl | 2015 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | ctrl | 2020 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | ctrl | 2030 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | ctrl | 2040 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | E | 7 | ctrl | 2050 | 1
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | Lower | 2020 | 96
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | Lower | 2050 | 96
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | Upper | 2020 | 99
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | Upper | 2050 | 99
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | ctrl | 2015 | 98
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | ctrl | 2020 | 98
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | ctrl | 2030 | 98
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | ctrl | 2040 | 98
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Round trip efficiency [%] | pct. |  | J | 2 | ctrl | 2050 | 98
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | Lower | 2020 | 30
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | Lower | 2050 | 30
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | Upper | 2020 | 50
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | Upper | 2050 | 50
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | ctrl | 2015 | 40
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | ctrl | 2020 | 40
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | ctrl | 2030 | 40
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | ctrl | 2040 | 40
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | F | 2 | ctrl | 2050 | 40
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | Lower | 2020 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | Lower | 2050 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | Upper | 2020 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | Upper | 2050 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | ctrl | 2015 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | ctrl | 2020 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | ctrl | 2030 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | ctrl | 2040 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 7 | ctrl | 2050 | 67.41
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | Lower | 2020 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | Lower | 2050 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | Upper | 2020 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | Upper | 2050 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | ctrl | 2015 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | ctrl | 2020 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | ctrl | 2030 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | ctrl | 2040 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 7 | ctrl | 2050 | 28.89
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | Lower | 2020 | 4.8764
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | Lower | 2050 | 4.8764
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | Upper | 2020 | 34.1351
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | Upper | 2050 | 34.1351
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | ctrl | 2015 | 8.8069
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | ctrl | 2020 | 8.8069
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | ctrl | 2030 | 8.8069
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | ctrl | 2040 | 8.8069
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/MWh Capacity/year] | EUR/MWh/year | 2020 | E | 7 | ctrl | 2050 | 8.8069
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | Lower | 2020 | 2.2112
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | Lower | 2050 | 2.2112
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | Upper | 2020 | 8.177
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | Upper | 2050 | 8.177
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | ctrl | 2015 | 3.0361
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | ctrl | 2020 | 3.0361
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | ctrl | 2030 | 3.0361
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | ctrl | 2040 | 3.0361
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Specific investment [M€/GWhCapacity] | MEUR/GWh | 2020 | H | [2, 7] | ctrl | 2050 | 3.0361
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | Lower | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | Lower | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | Upper | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | Upper | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | ctrl | 2015 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | ctrl | 2020 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | ctrl | 2030 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | ctrl | 2040 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWhoutput] | EUR/MWhoutput | 2020 | I | 7 | ctrl | 2050 | 0
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | Lower | 2020 | 1500
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | Lower | 2050 | 1500
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | Upper | 2020 | 5000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | Upper | 2050 | 5000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | ctrl | 2015 | 3000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | ctrl | 2020 | 3000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | ctrl | 2030 | 3000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | ctrl | 2040 | 3000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [m3] | m3 |  |  |  | ctrl | 2050 | 3000
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | Lower | 2020 | 30
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | Lower | 2050 | 30
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | Upper | 2020 | 60
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | Upper | 2050 | 60
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | ctrl | 2015 | 55
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | ctrl | 2020 | 55
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | ctrl | 2030 | 55
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | ctrl | 2040 | 55
141 Large hot water tank | Large-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  |  |  | ctrl | 2050 | 55
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Lower | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Lower | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Upper | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | Upper | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2015 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2030 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2040 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Charge efficiency [%] | pct. |  | B |  | ctrl | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2015 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2020 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2030 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2040 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2050 | 100
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Lower | 2020 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Lower | 2050 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Upper | 2020 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | Upper | 2050 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | Local
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | Upper | 2020 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | Upper | 2050 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2015 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2020 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2030 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2040 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2050 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | Upper | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | Upper | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | ctrl | 2015 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | ctrl | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | ctrl | 2030 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | ctrl | 2040 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Construction time [years] | years |  | F | 6 | ctrl | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | Lower | 2020 | 2.5
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | Lower | 2050 | 2.5
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | Upper | 2020 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | Upper | 2050 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | ctrl | 2015 | 2.1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | ctrl | 2020 | 2.1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | ctrl | 2030 | 2.1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | ctrl | 2040 | 2.1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy losses during storage [%/hour] | pct./hour |  | I |  | ctrl | 2050 | 2.1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | Lower | 2020 | 2
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | Lower | 2050 | 2
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | Upper | 2020 | 19
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | Upper | 2050 | 19
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | ctrl | 2015 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | ctrl | 2020 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | ctrl | 2030 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | ctrl | 2040 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Energy storage capacity for one unit [kWh] | kWh |  | A |  | ctrl | 2050 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | Upper | 2020 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | Upper | 2050 | 3
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | ctrl | 2015 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | ctrl | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | ctrl | 2030 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | ctrl | 2040 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Forced outage [%] | pct. |  |  | 5 | ctrl | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Heat
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | Lower | 2020 | 10
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | Lower | 2050 | 10
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | Upper | 2020 | 40
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | Upper | 2050 | 40
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2015 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2020 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2030 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2040 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Input capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2050 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | Lower | 2020 | 10
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | Lower | 2050 | 10
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | Upper | 2020 | 40
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | Upper | 2050 | 40
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2015 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2020 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2030 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2040 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Output capacity for one unit [kW] | kW |  |  | 5 | ctrl | 2050 | 20
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Upper | 2020 | 4
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Upper | 2050 | 4
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2015 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2020 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2030 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2040 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2050 | 1
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | Lower | 2020 | 15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | Lower | 2050 | 15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | Upper | 2020 | 50
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | Upper | 2050 | 50
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | ctrl | 2015 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | ctrl | 2020 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | ctrl | 2030 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | ctrl | 2040 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Energy/technical data | Technical lifetime [years] | years |  | E | 5 | ctrl | 2050 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | Lower | 2020 | 38.52
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | Lower | 2050 | 38.52
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | Upper | 2020 | 33.705
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | Upper | 2050 | 33.705
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | ctrl | 2015 | 48.15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | ctrl | 2020 | 48.15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | ctrl | 2030 | 48.15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | ctrl | 2040 | 48.15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof equipment [%] | pct. |  |  | 6 | ctrl | 2050 | 48.15
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | Lower | 2020 | 59.2052
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | Lower | 2050 | 59.2052
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | Upper | 2020 | 63.8421
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | Upper | 2050 | 63.8421
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | ctrl | 2015 | 49.9316
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | ctrl | 2020 | 49.9316
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | ctrl | 2030 | 49.9316
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | ctrl | 2040 | 49.9316
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - hereof installation [%] | pct. |  |  | 6 | ctrl | 2050 | 49.9316
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | Upper | 2020 | 0.71684
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | Upper | 2050 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | ctrl | 2015 | 0.61443
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | ctrl | 2020 | 0.71684
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | ctrl | 2030 | 1.0241
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | ctrl | 2040 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is electricity costs [€/MWh] | EUR/MWh | 2020 | K |  | ctrl | 2050 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | Upper | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | Upper | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2015 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2030 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2040 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | - of which is other O&M costs [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | Lower | 2020 | 25.6014
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | Lower | 2050 | 25.6014
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | Upper | 2020 | 81.9243
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | Upper | 2050 | 81.9243
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | ctrl | 2015 | 51.2027
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | ctrl | 2020 | 51.2027
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | ctrl | 2030 | 51.2027
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | ctrl | 2040 | 51.2027
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Fixed O&M [€/tank/year] | EUR/tank/year | 2020 | D | [5, 6] | ctrl | 2050 | 51.2027
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | Lower | 2020 | 522.2676
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | Lower | 2050 | 522.2676
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | Upper | 2020 | 133.127
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | Upper | 2050 | 133.127
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | ctrl | 2015 | 419.8622
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | ctrl | 2020 | 419.8622
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | ctrl | 2030 | 419.8622
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | ctrl | 2040 | 419.8622
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Specific investment [€/kWh] | EUR/kWh | 2020 | [F, G, L] | [5, 6] | ctrl | 2050 | 419.8622
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | Lower | 2020 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | Lower | 2050 | 0
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | Upper | 2020 | 0.71684
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | Upper | 2050 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | ctrl | 2015 | 0.61443
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | ctrl | 2020 | 0.71684
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | ctrl | 2030 | 1.0241
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | ctrl | 2040 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H | 6 | ctrl | 2050 | 1.2289
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | Lower | 2020 | 97
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | Lower | 2050 | 97
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | Upper | 2020 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | Upper | 2050 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | ctrl | 2015 | 92
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | ctrl | 2020 | 92
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | ctrl | 2030 | 92
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | ctrl | 2040 | 92
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Efficiency at typical cycle period [%] | pct. |  | [I, B] |  | ctrl | 2050 | 92
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | Lower | 2020 | 50
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | Lower | 2050 | 50
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | Upper | 2020 | 300
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | Upper | 2050 | 300
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | ctrl | 2015 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | ctrl | 2020 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | ctrl | 2030 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | ctrl | 2040 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Tank volume of example [l] | l |  |  |  | ctrl | 2050 | 90
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | Lower | 2020 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | Lower | 2050 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | Upper | 2020 | 60
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | Upper | 2050 | 60
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | ctrl | 2015 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | ctrl | 2020 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | ctrl | 2030 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | ctrl | 2040 | 30
142 Small scale hot water tank | Small-Scale Hot Water Tanks (steel) | Technology-specific data | Typical temperature difference in storage [hot/cold, K] | hot/cold,K |  | A | 8 | ctrl | 2050 | 30
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | System
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2020 | 1100
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2030 | 1100
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2040 | 1100
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  |  | ctrl | 2050 | 1100
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Chemical
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Chemical
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Chemical
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Chemical
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Input capacity for one unit [MW] | MW |  |  |  | ctrl | 2020 | 2200
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Input capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | 2200
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Input capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | 2200
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Input capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | 2200
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2020 | 6600
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | 6600
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | 6600
150 Underground Storage of Gas | Natural gas storage underground | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | 6600
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  |  | ctrl | 2020 | 1.2698
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  |  | ctrl | 2030 | 1.2698
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  |  | ctrl | 2040 | 1.2698
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  |  | ctrl | 2050 | 1.2698
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2020 | 2.6067e-06
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2030 | 2.6067e-06
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2040 | 2.6067e-06
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2050 | 2.6067e-06
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2020 | 0.00023656
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2030 | 0.00023656
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2040 | 0.00023656
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  |  | ctrl | 2050 | 0.00023656
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2020 | -
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2030 | -
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2040 | -
150 Underground Storage of Gas | Natural gas storage underground | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2050 | -
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Compressors, incl. Auxiliaries [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 32.0479
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Compressors, incl. Auxiliaries [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 32.0479
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Compressors, incl. Auxiliaries [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 32.0479
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Compressors, incl. Auxiliaries [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 32.0479
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Connections, transformer, regulation, and instruments [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 13.4781
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Connections, transformer, regulation, and instruments [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 13.4781
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Connections, transformer, regulation, and instruments [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 13.4781
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Connections, transformer, regulation, and instruments [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 13.4781
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction and equipment [M€] | MEUR | 2020 | B |  | ctrl | 2020 | 23.5118
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction and equipment [M€] | MEUR | 2020 | B |  | ctrl | 2030 | 23.5118
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction and equipment [M€] | MEUR | 2020 | B |  | ctrl | 2040 | 23.5118
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction and equipment [M€] | MEUR | 2020 | B |  | ctrl | 2050 | 23.5118
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction work [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 2.9951
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction work [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 2.9951
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction work [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 2.9951
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Construction work [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 2.9951
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Cushion gas for one cavern (40% of total) [M€] | MEUR | 2020 | B |  | ctrl | 2020 | 14.9757
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Cushion gas for one cavern (40% of total) [M€] | MEUR | 2020 | B |  | ctrl | 2030 | 14.9757
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Cushion gas for one cavern (40% of total) [M€] | MEUR | 2020 | B |  | ctrl | 2040 | 14.9757
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Cushion gas for one cavern (40% of total) [M€] | MEUR | 2020 | B |  | ctrl | 2050 | 14.9757
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Plant for cavern leaching [M€] | MEUR | 2020 |  |  | ctrl | 2020 | 10.5277
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Plant for cavern leaching [M€] | MEUR | 2020 |  |  | ctrl | 2030 | 10.5277
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Plant for cavern leaching [M€] | MEUR | 2020 |  |  | ctrl | 2040 | 10.5277
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Plant for cavern leaching [M€] | MEUR | 2020 |  |  | ctrl | 2050 | 10.5277
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total cost [M€] | MEUR | 2020 | B |  | ctrl | 2020 | 38.4874
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total cost [M€] | MEUR | 2020 | B |  | ctrl | 2030 | 38.4874
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total cost [M€] | MEUR | 2020 | B |  | ctrl | 2040 | 38.4874
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total cost [M€] | MEUR | 2020 | B |  | ctrl | 2050 | 38.4874
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total investment cost [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 67.0909
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total investment cost [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 67.0909
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total investment cost [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 67.0909
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Total investment cost [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 67.0909
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Udtrækstog [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 13.7776
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Udtrækstog [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 13.7776
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Udtrækstog [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 13.7776
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Udtrækstog [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 13.7776
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Withdrawal equipment [M€] | MEUR | 2020 | A |  | ctrl | 2020 | 4.7922
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Withdrawal equipment [M€] | MEUR | 2020 | A |  | ctrl | 2030 | 4.7922
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Withdrawal equipment [M€] | MEUR | 2020 | A |  | ctrl | 2040 | 4.7922
150 Underground Storage of Gas | Natural gas storage underground | Technology-specific data | Withdrawal equipment [M€] | MEUR | 2020 | A |  | ctrl | 2050 | 4.7922
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | Lower | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | Lower | 2050 | 0.89746
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | Upper | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | Upper | 2050 | 0.90242
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | ctrl | 2019 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | ctrl | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | ctrl | 2030 | 0.88962
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | ctrl | 2040 | 0.89647
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Charge efficiency [%] | pct. |  | D |  | ctrl | 2050 | 0.90242
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | Lower | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | Lower | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | Upper | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | Upper | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | ctrl | 2019 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | ctrl | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | ctrl | 2030 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | ctrl | 2040 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | - Discharge efficiency [%] | pct. |  | E |  | ctrl | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | Lower | 2020 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | Lower | 2050 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | Upper | 2020 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | Upper | 2050 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | ctrl | 2019 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | ctrl | 2020 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | ctrl | 2030 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | ctrl | 2040 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Application |  |  | L |  | ctrl | 2050 | Local
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | Lower | 2020 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | Lower | 2050 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | Upper | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | Upper | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | ctrl | 2019 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | ctrl | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | ctrl | 2030 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | ctrl | 2040 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | J |  | ctrl | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | Lower | 2020 | 0.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | Lower | 2050 | 0.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | Upper | 2020 | 0.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | Upper | 2050 | 0.2
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | ctrl | 2019 | 0.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | ctrl | 2020 | 0.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | ctrl | 2030 | 0.4
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | ctrl | 2040 | 0.4
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Construction time [years] | years |  |  | 3 | ctrl | 2050 | 0.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | Lower | 2020 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | Lower | 2050 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | Upper | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | Upper | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | ctrl | 2019 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | ctrl | 2020 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | ctrl | 2030 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | ctrl | 2040 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | F, K |  | ctrl | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | Lower | 2020 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | Lower | 2050 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | Upper | 2020 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | Upper | 2050 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | ctrl | 2019 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | ctrl | 2020 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | ctrl | 2030 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | ctrl | 2040 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  |  | 1 | ctrl | 2050 | 16.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | Lower | 2020 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | Lower | 2050 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | Upper | 2020 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | Upper | 2050 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | ctrl | 2019 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | ctrl | 2020 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | ctrl | 2030 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | ctrl | 2040 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Forced outage [%] | pct. |  | I |  | ctrl | 2050 | 0
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2019 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Chemical
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | Lower | 2020 | 0.1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | Lower | 2050 | 0.085
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | Upper | 2020 | 0.99
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | Upper | 2050 | 0.08
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | ctrl | 2019 | 0.1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | ctrl | 2020 | 0.095
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | ctrl | 2030 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | ctrl | 2040 | 0.08
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | [1, 2] | ctrl | 2050 | 0.08
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | Lower | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | Lower | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | Upper | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | Upper | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | ctrl | 2019 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | ctrl | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | ctrl | 2030 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | ctrl | 2040 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A |  | ctrl | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | Lower | 2020 | 3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | Lower | 2050 | 1.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | Upper | 2020 | 3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | Upper | 2050 | 0.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | ctrl | 2019 | 3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | ctrl | 2020 | 3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | ctrl | 2030 | 2
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | ctrl | 2040 | 1.5
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | G | 3 | ctrl | 2050 | 1
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | Lower | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | Lower | 2050 | 0.89746
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | Upper | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | Upper | 2050 | 0.90242
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | ctrl | 2019 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | ctrl | 2020 | 0.88288
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | ctrl | 2030 | 0.88962
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | ctrl | 2040 | 0.89647
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 1 | ctrl | 2050 | 0.90242
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | Lower | 2020 | 25
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | Lower | 2050 | 30
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | Upper | 2020 | 25
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | Upper | 2050 | 30
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2019 | 25
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2020 | 25
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2030 | 30
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2040 | 30
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Energy/technical data | Technical lifetime [years] | years |  |  |  | ctrl | 2050 | 30
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2020 | 0.031902
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2050 | 0.016962
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2020 | 0.031902
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2050 | 0.0084811
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2019 | 0.031902
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2020 | 0.031902
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2030 | 0.025443
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2040 | 0.013528
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Compressor component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2050 | 0.0084811
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | Lower | 2020 | 638.04
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | Lower | 2050 | 478.53
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | Upper | 2020 | 638.04
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | Upper | 2050 | 319.02
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | ctrl | 2019 | 638.04
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | ctrl | 2020 | 638.04
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | ctrl | 2030 | 531.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | ctrl | 2040 | 531.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 |  | 1 | ctrl | 2050 | 425.36
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2020 | 0.0095706
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2050 | 0.007633
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2020 | 0.0095706
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2050 | 0.0050887
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2019 | 0.0095706
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2020 | 0.0095706
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2030 | 0.0084472
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2040 | 0.0067171
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Installation, equipment, manhours [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2050 | 0.0050887
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2020 | 0.060614
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2050 | 0.037485
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2020 | 0.060614
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2050 | 0.022331
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2019 | 0.060614
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2020 | 0.060614
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2030 | 0.047757
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2040 | 0.028765
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2050 | 0.022331
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2020 | 0.019141
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Lower | 2050 | 0.015266
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2020 | 0.019141
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | Upper | 2050 | 0.010177
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2019 | 0.019141
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2020 | 0.019141
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2030 | 0.016894
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2040 | 0.011857
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Type I tanks component [M€/MWh] | MEUR/MWh | 2020 |  | 1 | ctrl | 2050 | 0.010177
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | Lower | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | Lower | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | Upper | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | Upper | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2019 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2020 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2030 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2040 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 |  |  | ctrl | 2050 | -
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | Lower | 2020 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | Lower | 2050 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | Upper | 2020 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | Upper | 2050 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | ctrl | 2019 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | ctrl | 2020 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | ctrl | 2030 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | ctrl | 2040 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | H | 3 | ctrl | 2050 | 3.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | Lower | 2020 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | Lower | 2050 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | Upper | 2020 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | Upper | 2050 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | ctrl | 2019 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | ctrl | 2020 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | ctrl | 2030 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | ctrl | 2040 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Regulation ability | Secondary regulation [%/minute] | pct./minute |  | H | 3 | ctrl | 2050 | 6.7
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | Lower | 2020 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | Lower | 2050 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | Upper | 2020 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | Upper | 2050 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | ctrl | 2019 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | ctrl | 2020 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | ctrl | 2030 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | ctrl | 2040 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Gravimetric energy density [kWh/kg] | kWh/kg |  |  |  | ctrl | 2050 | 33.3
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | Lower | 2020 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | Lower | 2050 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | Upper | 2020 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | Upper | 2050 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | ctrl | 2019 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | ctrl | 2020 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | ctrl | 2030 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | ctrl | 2040 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  |  | 4 | ctrl | 2050 | 2.84×10-27
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | Lower | 2020 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | Lower | 2050 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | Upper | 2020 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | Upper | 2050 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | ctrl | 2019 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | ctrl | 2020 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | ctrl | 2030 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | ctrl | 2040 | 0.09
151a Hydrogen Storage - Tanks | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar) | Technology-specific data | Volumetric energy density @0oC and 1atm pressure [kWh/m3] | kWh/m3 |  |  |  | ctrl | 2050 | 0.09
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Charge efficiency [%] | pct. |  | I |  | ctrl | 2015 | 0.72
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Charge efficiency [%] | pct. |  | I |  | ctrl | 2020 | 0.72
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Charge efficiency [%] | pct. |  | I |  | ctrl | 2030 | 0.74
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Charge efficiency [%] | pct. |  | I |  | ctrl | 2040 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Charge efficiency [%] | pct. |  | I |  | ctrl | 2050 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | Lower | 2020 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | Lower | 2050 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | Upper | 2020 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | Upper | 2050 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | ctrl | 2015 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | ctrl | 2020 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | ctrl | 2030 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | ctrl | 2040 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 47 | ctrl | 2050 | 1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Lower | 2020 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Lower | 2050 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Upper | 2020 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Upper | 2050 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2015 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2020 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2030 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2040 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2050 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | Lower | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | Upper | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2015 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2030 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2040 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Construction time [years] | years |  |  |  | ctrl | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | Lower | 2020 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | Lower | 2050 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | Upper | 2020 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | Upper | 2050 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | ctrl | 2015 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | ctrl | 2020 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | ctrl | 2030 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | ctrl | 2040 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | 9 | ctrl | 2050 | 0.01
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Lower | 2020 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Lower | 2050 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Upper | 2020 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | Upper | 2050 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2015 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2020 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2030 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2040 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A |  | ctrl | 2050 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2020 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2050 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2020 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2050 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2015 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2020 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2030 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2040 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2050 | 0
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Chemical
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | Lower | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | Lower | 2050 | 50
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | Upper | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | Upper | 2050 | 500
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | ctrl | 2015 | 0.3
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | ctrl | 2020 | 7
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | ctrl | 2030 | 34
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | ctrl | 2040 | 70
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Input capacity for one unit [MW] | MW |  | B |  | ctrl | 2050 | 300
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Lower | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Lower | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Upper | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Upper | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2015 | 0.1
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | 5
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | 10
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | 50
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | Lower | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | Lower | 2050 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | Upper | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | Upper | 2050 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | ctrl | 2015 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | ctrl | 2020 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | ctrl | 2030 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | ctrl | 2040 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  | 47 | ctrl | 2050 | 2
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | Lower | 2020 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | Lower | 2050 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | Upper | 2020 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | Upper | 2050 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | ctrl | 2015 | 0.72
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | ctrl | 2020 | 0.72
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | ctrl | 2030 | 0.74
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | ctrl | 2040 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Round trip efficiency [%] | pct. |  | C | 47 | ctrl | 2050 | 0.75
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | Lower | 2020 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | Lower | 2050 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | Upper | 2020 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | Upper | 2050 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | ctrl | 2015 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | ctrl | 2020 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | ctrl | 2030 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | ctrl | 2040 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Energy/technical data | Technical lifetime [years] | years |  |  | 47 | ctrl | 2050 | 20
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | Lower | 2020 | 0.0005317
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | Lower | 2050 | 0.00025522
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | Upper | 2020 | 0.0005317
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | Upper | 2050 | 0.00019141
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2015 | 0.0005317
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2020 | 0.0005317
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2030 | 0.00031902
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2040 | 0.00030532
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2050 | 0.00025522
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | Lower | 2020 | 0.00036156
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | Lower | 2050 | 0.00017014
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | Upper | 2020 | 0.00036156
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | Upper | 2050 | 0.00012761
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2015 | 0.00036156
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2020 | 0.00036156
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2030 | 0.00021268
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2040 | 0.00019141
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 | F |  | ctrl | 2050 | 0.00017014
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | Lower | 2020 | 3.7996e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | Lower | 2050 | 1.8093e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | Upper | 2020 | 3.7996e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | Upper | 2050 | 1.357e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | ctrl | 2015 | 3.7996e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | ctrl | 2020 | 3.7996e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | ctrl | 2030 | 2.2616e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | ctrl | 2040 | 2.0355e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G |  | ctrl | 2050 | 1.8093e-05
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | Lower | 2020 | 0.00089326
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | Lower | 2050 | 0.00042536
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | Upper | 2020 | 0.00089326
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | Upper | 2050 | 0.00031902
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | ctrl | 2015 | 0.00089326
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | ctrl | 2020 | 0.00089326
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | ctrl | 2030 | 0.0005317
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | ctrl | 2040 | 0.00047853
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E |  | ctrl | 2050 | 0.00042536
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Lower | 2020 | 9.4989e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Lower | 2050 | 4.5233e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Upper | 2020 | 9.4989e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Upper | 2050 | 3.3925e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2015 | 9.4989e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2020 | 9.4989e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2030 | 5.6541e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2040 | 5.0887e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2050 | 4.5233e-06
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | D |  | ctrl | 2015 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | D |  | ctrl | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | D |  | ctrl | 2030 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | D |  | ctrl | 2040 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | D |  | ctrl | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2015 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2020 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2030 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2040 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2050 | -
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | Lower | 2020 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | Lower | 2050 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | Upper | 2020 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | Upper | 2050 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | ctrl | 2015 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | ctrl | 2020 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | ctrl | 2030 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | ctrl | 2040 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  |  | 43 | ctrl | 2050 | 1900
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | Lower | 2020 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | Lower | 2050 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | Upper | 2020 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | Upper | 2050 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | ctrl | 2015 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | ctrl | 2020 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | ctrl | 2030 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | ctrl | 2040 | 2080
151b Hydrogen Storage - LOHC | Hydrogen storage - LOHC | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  |  | 43 | ctrl | 2050 | 2080
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | Lower | 2020 | 0.98
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | Lower | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | Upper | 2020 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | Upper | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2015 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2020 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2030 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2040 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Charge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | Lower | 2020 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | Lower | 2050 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | Upper | 2020 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | Upper | 2050 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2015 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2020 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2030 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2040 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | 54-57 | ctrl | 2050 | 1
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | Lower | 2020 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | Lower | 2050 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | Upper | 2020 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | Upper | 2050 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | Local
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Lower | 2020 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Lower | 2050 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Upper | 2020 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | Upper | 2050 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2015 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2020 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2030 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2040 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2050 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | Lower | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | Upper | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2015 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2030 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2040 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Construction time [years] | years |  | E |  | ctrl | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | Lower | 2020 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | Lower | 2050 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | Upper | 2020 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | Upper | 2050 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | ctrl | 2015 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | ctrl | 2020 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | ctrl | 2030 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | ctrl | 2040 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy losses during storage [%/period] | pct./period |  | C |  | ctrl | 2050 | 0.01
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | Lower | 2020 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | Lower | 2050 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | Upper | 2020 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | Upper | 2050 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | ctrl | 2015 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | ctrl | 2020 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | ctrl | 2030 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | ctrl | 2040 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | 54-57 | ctrl | 2050 | 150000
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2020 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | Lower | 2050 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2020 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | Upper | 2050 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2015 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2020 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2030 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2040 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Forced outage [%] | pct. |  |  |  | ctrl | 2050 | 0
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Chemical
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | Lower | 2020 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | Lower | 2050 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | Upper | 2020 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | Upper | 2050 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | ctrl | 2015 | 180
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | ctrl | 2020 | 175
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | ctrl | 2030 | 170
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | ctrl | 2040 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Input capacity for one unit [MW] | MW |  | B | 54-57 | ctrl | 2050 | 150
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Lower | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Lower | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Upper | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | Upper | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2015 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2030 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2040 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Output capacity for one unit [MW] | MW |  |  |  | ctrl | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Lower | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Lower | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Upper | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | Upper | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2015 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2030 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2040 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D |  | ctrl | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | Lower | 2020 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | Lower | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | Upper | 2020 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | Upper | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | ctrl | 2015 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | ctrl | 2020 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | ctrl | 2030 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | ctrl | 2040 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Round trip efficiency [%] | pct. |  |  | 54-57 | ctrl | 2050 | 0.99
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | Lower | 2020 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | Lower | 2050 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | Upper | 2020 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | Upper | 2050 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | ctrl | 2015 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | ctrl | 2020 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | ctrl | 2030 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | ctrl | 2040 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Energy/technical data | Technical lifetime [years] | years |  |  | 57 | ctrl | 2050 | 100
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2020 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2050 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2020 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2050 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2015 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2020 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2030 | 0.00063804
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2040 | 0.0005317
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof equipment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2050 | 0.00042536
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2020 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2050 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2020 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2050 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2015 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2020 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2030 | 0.0012761
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2040 | 0.00095706
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | - hereof installation [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2050 | 0.00074438
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | Lower | 2020 | 6.7849e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | Lower | 2050 | 4.071e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | Upper | 2020 | 6.7849e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | Upper | 2050 | 2.2616e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | ctrl | 2015 | 6.7849e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | ctrl | 2020 | 6.7849e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | ctrl | 2030 | 4.5233e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | ctrl | 2040 | 3.3925e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | G | 57 | ctrl | 2050 | 2.714e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2020 | 0.0031902
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Lower | 2050 | 0.0019141
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2020 | 0.0031902
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | Upper | 2050 | 0.0010634
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2015 | 0.0031902
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2020 | 0.0031902
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2030 | 0.0021268
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2040 | 0.0015951
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 |  | 59 | ctrl | 2050 | 0.0012761
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Lower | 2020 | 3.6075e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Lower | 2050 | 2.1645e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Upper | 2020 | 3.6075e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | Upper | 2050 | 1.2025e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2015 | 3.6075e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2020 | 3.6075e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2030 | 2.405e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2040 | 1.8038e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | H |  | ctrl | 2050 | 1.443e-05
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | Lower | 2020 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | Lower | 2050 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | Upper | 2020 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | Upper | 2050 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | ctrl | 2015 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | ctrl | 2020 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | ctrl | 2030 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | ctrl | 2040 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Primary regulation [%/30 sec] | pct./30sec |  | F |  | ctrl | 2050 | 3.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | Lower | 2020 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | Lower | 2050 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | Upper | 2020 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | Upper | 2050 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2015 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2020 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2030 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2040 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Regulation ability | Secondary regulation [%/minute] | pct./minute |  |  |  | ctrl | 2050 | 6.7
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | Lower | 2020 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | Lower | 2050 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | Upper | 2020 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | Upper | 2050 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | ctrl | 2015 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | ctrl | 2020 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | ctrl | 2030 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | ctrl | 2040 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Gravimetric energy density [Wh/kg] | Wh/kg |  | I |  | ctrl | 2050 | 33.3
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | Lower | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | Lower | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | Upper | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | Upper | 2050 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | ctrl | 2015 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | ctrl | 2020 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | ctrl | 2030 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | ctrl | 2040 | -
151c Hydrogen Storage - Caverns | Hydrogen storage - caverns | Technology-specific data | Permeation characteristics [mol/s/m/MPa1/2] | mol/s/m/MPa1/2 |  | J |  | ctrl | 2050 | -
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | Lower | 2020 | 2
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | Lower | 2050 | 2
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | Upper | 2020 | 3
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | Upper | 2050 | 3
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | ctrl | 2015 | 2.5
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | ctrl | 2020 | 2.5
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | ctrl | 2030 | 2.5
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Construction time [years] | years |  | A |  | ctrl | 2050 | 2.5
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Mechanical
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | Lower | 2020 | 10
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | Lower | 2050 | 10
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | Upper | 2020 | 1000
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | Upper | 2050 | 1000
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | ctrl | 2015 | 500
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | ctrl | 2020 | 500
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | ctrl | 2030 | 500
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Generating capacity for one unit [MW] | MW |  | A | 2 | ctrl | 2050 | 500
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Technical lifetime [years] | years |  | A | 1 | ctrl | 2015 | 50
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Technical lifetime [years] | years |  | A | 1 | ctrl | 2020 | 50
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Technical lifetime [years] | years |  | A | 1 | ctrl | 2030 | 50
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Technical lifetime [years] | years |  | A | 1 | ctrl | 2050 | 50
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | Lower | 2020 | 70
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | Lower | 2050 | 70
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | Upper | 2020 | 80
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | Upper | 2050 | 80
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | ctrl | 2015 | 75
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | ctrl | 2020 | 75
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | ctrl | 2030 | 75
160 Pumped hydro storage | Pumped hydro storage | Energy/technical data | Total efficiency [%] net | pct. |  | A | 1 | ctrl | 2050 | 75
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | Lower | 2020 | 6380.4
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | Lower | 2050 | 6380.4
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | Upper | 2020 | 12760.8
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | Upper | 2050 | 12760.8
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | ctrl | 2015 | 8507.2
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | ctrl | 2020 | 8507.2
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | ctrl | 2030 | 8507.2
160 Pumped hydro storage | Pumped hydro storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | [B, A] | 3 | ctrl | 2050 | 8507.2
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | Lower | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | Lower | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | Upper | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | Upper | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | ctrl | 2015 | 0.63804
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | ctrl | 2020 | 0.63804
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | ctrl | 2030 | 0.63804
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, pump part [M€/MW] | MEUR/MW | 2020 | [B, C, A] | 1&2 | ctrl | 2050 | 0.63804
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | Lower | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | Lower | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | Upper | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | Upper | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | ctrl | 2015 | 4.2536
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | ctrl | 2020 | 4.2536
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | ctrl | 2030 | 4.2536
160 Pumped hydro storage | Pumped hydro storage | Financial data | Investment, total, greenfield plant [M€/MW] | MEUR/MW | 2020 | [D, A] | 4 | ctrl | 2050 | 4.2536
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | Lower | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | Lower | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | Upper | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | Upper | 2050 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | ctrl | 2015 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | ctrl | 2020 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | ctrl | 2030 | 0
160 Pumped hydro storage | Pumped hydro storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 |  | ctrl | 2050 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | Lower | 2020 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | Lower | 2050 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | Upper | 2020 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | Upper | 2050 | 85
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | ctrl | 2015 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | ctrl | 2020 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | ctrl | 2030 | 84
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Charge efficiency [%] | pct. |  |  | [7] | ctrl | 2050 | 85
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | Lower | 2020 | 69
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | Lower | 2050 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | Upper | 2020 | 69
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | Upper | 2050 | 85
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | ctrl | 2015 | 69
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | ctrl | 2020 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | ctrl | 2030 | 84
161 CAES | Compressed Air Energy Storage | Energy/technical data | - Discharge efficiency [%] | pct. |  |  | [7] | ctrl | 2050 | 85
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System, energy-intensive
161 CAES | Compressed Air Energy Storage | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2015 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2030 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  |  |  | ctrl | 2050 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | Lower | 2020 | 2
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | Lower | 2050 | 2
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | Upper | 2020 | 3
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | Upper | 2050 | 3
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | ctrl | 2015 | 2.5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | ctrl | 2020 | 2.5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | ctrl | 2030 | 2.5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Construction time [years] | years |  |  | [8] | ctrl | 2050 | 2.5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | Lower | 2020 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | Lower | 2050 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | Upper | 2020 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | Upper | 2050 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | ctrl | 2015 | 0.1
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | ctrl | 2020 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | ctrl | 2030 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy losses during storage [%/period] | pct./period |  |  | [27] | ctrl | 2050 | 0
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | Lower | 2050 | 3000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | Upper | 2050 | 10000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | ctrl | 2015 | 3000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | ctrl | 2020 | 3000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | ctrl | 2030 | 3000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | I | [3] | ctrl | 2050 | 3000
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | Lower | 2050 | 2
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | Upper | 2050 | 4
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | ctrl | 2015 | 5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | ctrl | 2020 | 5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | ctrl | 2030 | 4
161 CAES | Compressed Air Energy Storage | Energy/technical data | Forced outage [%] | pct. |  | I, K | [9] | ctrl | 2050 | 4
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Mechanical
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | Lower | 2050 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | Upper | 2050 | 80
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | ctrl | 2015 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | ctrl | 2020 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | ctrl | 2030 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Input capacity for one unit [MW] | MW |  | I, J | [9] | ctrl | 2050 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | Lower | 2050 | 300
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | Upper | 2050 | 500
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | ctrl | 2015 | 300
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | ctrl | 2020 | 300
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | ctrl | 2030 | 300
161 CAES | Compressed Air Energy Storage | Energy/technical data | Output capacity for one unit [MW] | MW |  | I, J | [3] | ctrl | 2050 | 300
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | Lower | 2050 | 2
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | Upper | 2050 | 3
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | ctrl | 2015 | 5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | ctrl | 2020 | 5
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | ctrl | 2030 | 4
161 CAES | Compressed Air Energy Storage | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | I, K | [9] | ctrl | 2050 | 3
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | Lower | 2020 | 55
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | Lower | 2050 | 64
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | Upper | 2020 | 55
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | Upper | 2050 | 72
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | ctrl | 2015 | 55
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | ctrl | 2020 | 60
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | ctrl | 2030 | 70
161 CAES | Compressed Air Energy Storage | Energy/technical data | Round trip efficiency [%] | pct. |  | A, B | [9] [26] | ctrl | 2050 | 72
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | Lower | 2020 | 35
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | Lower | 2050 | 35
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | Upper | 2020 | 45
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | Upper | 2050 | 45
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | ctrl | 2015 | 40
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | ctrl | 2020 | 40
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | ctrl | 2030 | 40
161 CAES | Compressed Air Energy Storage | Energy/technical data | Technical lifetime [years] | years |  |  | [20] [8] | ctrl | 2050 | 40
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | Lower | 2020 | 0.31902
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | Lower | 2050 | 0.31902
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | Upper | 2020 | 1.2761
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | Upper | 2050 | 1.2761
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | ctrl | 2015 | 0.63804
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | ctrl | 2020 | 0.63804
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | ctrl | 2030 | 0.95706
161 CAES | Compressed Air Energy Storage | Financial data | - Capacity component [M€/MW] | MEUR/MW | 2020 | 0 | [24] | ctrl | 2050 | 0.95706
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | Lower | 2020 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | Lower | 2050 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | Upper | 2020 | 0.010634
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | Upper | 2050 | 0.010634
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | ctrl | 2015 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | ctrl | 2020 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | ctrl | 2030 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Energy component [M€/MWh] | MEUR/MWh | 2020 | H | [23] | ctrl | 2050 | 0.0021268
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | Lower | 2020 | 0.085072
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | Lower | 2050 | 0.085072
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | Upper | 2020 | 0.095706
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | Upper | 2050 | 0.095706
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | ctrl | 2015 | 0.090389
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | ctrl | 2020 | 0.090389
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | ctrl | 2030 | 0.090389
161 CAES | Compressed Air Energy Storage | Financial data | - Other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [24] | ctrl | 2050 | 0.090389
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | Lower | 2020 | 2126.8
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | Lower | 2050 | 2126.8
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | Upper | 2020 | 4253.6
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | Upper | 2050 | 4253.6
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | ctrl | 2015 | 2615.964
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | ctrl | 2020 | 2615.964
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | ctrl | 2030 | 2615.964
161 CAES | Compressed Air Energy Storage | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | 0 | [20] | ctrl | 2050 | 2615.964
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | Lower | 2020 | 0.31902
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | Lower | 2050 | 0.42536
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | Upper | 2020 | 1.2761
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | Upper | 2050 | 2.1268
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | ctrl | 2015 | 0.69121
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | ctrl | 2020 | 0.69121
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | ctrl | 2030 | 1.0634
161 CAES | Compressed Air Energy Storage | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | C, E | Table 3 [26] | ctrl | 2050 | 0.85072
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | Lower | 2020 | 2.1268
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | Lower | 2050 | 2.1268
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | Upper | 2020 | 3.1902
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | Upper | 2050 | 3.1902
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | ctrl | 2015 | 2.616
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | ctrl | 2020 | 2.616
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | ctrl | 2030 | 2.616
161 CAES | Compressed Air Energy Storage | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [20] | ctrl | 2050 | 2.616
161 CAES | Compressed Air Energy Storage | Regulation ability | Full charge to full discharge [sec] | sec |  | F |  | ctrl | 2015 | -
161 CAES | Compressed Air Energy Storage | Regulation ability | Full charge to full discharge [sec] | sec |  | F |  | ctrl | 2020 | -
161 CAES | Compressed Air Energy Storage | Regulation ability | Full charge to full discharge [sec] | sec |  | F |  | ctrl | 2030 | -
161 CAES | Compressed Air Energy Storage | Regulation ability | Full charge to full discharge [sec] | sec |  | F |  | ctrl | 2050 | -
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | Lower | 2020 | 500
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | Lower | 2050 | 800
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | Upper | 2020 | 1000
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | Upper | 2050 | 1200
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | ctrl | 2015 | 700
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | ctrl | 2020 | 700
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | ctrl | 2030 | 1000
161 CAES | Compressed Air Energy Storage | Regulation ability | Idle to full discharge [sec] | sec |  | D, G | [3], [8] | ctrl | 2050 | 1000
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | Lower | 2020 | -
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | Lower | 2050 | 584.87
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | Upper | 2020 | -
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | Upper | 2050 | 680.576
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | ctrl | 2015 | 680.576
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | ctrl | 2020 | 680.576
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | ctrl | 2030 | 680.576
161 CAES | Compressed Air Energy Storage | Technology-specific data | Specific investment [€/kW] | EUR/kW | 2020 | C, K | Table 3 | ctrl | 2050 | 680.576
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | Lower | 2020 | 99
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | Lower | 2050 | 99
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | Upper | 2020 | 99.5
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | Upper | 2050 | 99.5
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | ctrl | 2020 | 99
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | ctrl | 2030 | 99
162 Flywheels | Flywheels | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | ctrl | 2050 | 99
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | Lower | 2020 | 99
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | Lower | 2050 | 99
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | Upper | 2020 | 99.5
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | Upper | 2050 | 99.5
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | ctrl | 2020 | 99
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | ctrl | 2030 | 99
162 Flywheels | Flywheels | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | ctrl | 2050 | 99
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System
162 Flywheels | Flywheels | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | Lower | 2020 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | Lower | 2050 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | Upper | 2020 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | Upper | 2050 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | ctrl | 2020 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | ctrl | 2030 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Construction time [years] | years |  | A, M |  | ctrl | 2050 | 0.25
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | Lower | 2020 | 2
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | Lower | 2050 | 0.5
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | Upper | 2020 | 5
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | Upper | 2050 | 1.5
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | ctrl | 2020 | 3
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | ctrl | 2030 | 1
162 Flywheels | Flywheels | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | ctrl | 2050 | 1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | Lower | 2020 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | Lower | 2050 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | Upper | 2020 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | Upper | 2050 | 0.15
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | ctrl | 2020 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | ctrl | 2030 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | ctrl | 2050 | 0.1
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Mechanical
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | Lower | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | Lower | 2050 | 1
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | Upper | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | Upper | 2050 | 1.5
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2030 | 1
162 Flywheels | Flywheels | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2050 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | Lower | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | Lower | 2050 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | Upper | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | Upper | 2050 | 1.5
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2020 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2030 | 1
162 Flywheels | Flywheels | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2050 | 1
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | Lower | 2020 | 98
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | Lower | 2050 | 98
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | Upper | 2020 | 99
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | Upper | 2050 | 99
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | ctrl | 2020 | 98
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | ctrl | 2030 | 98
162 Flywheels | Flywheels | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | ctrl | 2050 | 98
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | Lower | 2020 | 20
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | Lower | 2050 | 20
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | Upper | 2020 | 25
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | Upper | 2050 | 25
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | ctrl | 2020 | 20
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | ctrl | 2030 | 25
162 Flywheels | Flywheels | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | ctrl | 2050 | 25
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | Lower | 2020 | 0.10634
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | Lower | 2050 | 0.095706
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | Upper | 2020 | 0.10634
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | Upper | 2050 | 0.10634
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | ctrl | 2020 | 0.10634
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | ctrl | 2030 | 0.10634
162 Flywheels | Flywheels | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | ctrl | 2050 | 0.10634
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | Lower | 2020 | 0.31902
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | Lower | 2050 | 0.31902
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | Upper | 2020 | 0.38282
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | Upper | 2050 | 0.38282
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | ctrl | 2020 | 0.35092
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | ctrl | 2030 | 0.35092
162 Flywheels | Flywheels | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | ctrl | 2050 | 0.35092
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | Lower | 2020 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | Lower | 2050 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | Upper | 2020 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | Upper | 2050 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | ctrl | 2020 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | ctrl | 2030 | 797.55
162 Flywheels | Flywheels | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | ctrl | 2050 | 797.55
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | Lower | 2020 | 0.31902
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | Lower | 2050 | 0.31902
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | Upper | 2020 | 0.38282
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | Upper | 2050 | 0.38282
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | ctrl | 2020 | 0.35624
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | ctrl | 2030 | 0.35624
162 Flywheels | Flywheels | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | ctrl | 2050 | 0.35624
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | Lower | 2020 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | Lower | 2050 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | Upper | 2020 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | Upper | 2050 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | ctrl | 2020 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | ctrl | 2030 | 0
162 Flywheels | Flywheels | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | ctrl | 2050 | 0
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | Lower | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | Lower | 2050 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | Upper | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | Upper | 2050 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2030 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2050 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | Lower | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | Lower | 2050 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | Upper | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | Upper | 2050 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2020 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2030 | 0.003
162 Flywheels | Flywheels | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2050 | 0.003
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | Lower | 2020 | 106
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | Lower | 2050 | 106
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | Upper | 2020 | 107
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | Upper | 2050 | 107
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | ctrl | 2020 | 106
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | ctrl | 2030 | 106
162 Flywheels | Flywheels | Technology-specific data | Cycle life |  |  | A |  | ctrl | 2050 | 106
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | Lower | 2020 | 300
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | Lower | 2050 | 350
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | Upper | 2020 | 400
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | Upper | 2050 | 400
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | ctrl | 2020 | 350
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | ctrl | 2030 | 350
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | ctrl | 2050 | 350
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | Lower | 2020 | 1300
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | Lower | 2050 | 1300
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | Upper | 2020 | 2000
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | Upper | 2050 | 2000
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | ctrl | 2020 | 1500
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | ctrl | 2030 | 1500
162 Flywheels | Flywheels | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | ctrl | 2050 | 1500
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | Lower | 2020 | 0.14888
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | Lower | 2050 | 0.13824
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | Upper | 2020 | 0.15951
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | Upper | 2050 | 0.14888
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | ctrl | 2020 | 0.15419
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | ctrl | 2030 | 0.14462
162 Flywheels | Flywheels | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | ctrl | 2050 | 0.13931
162 Flywheels | Technology | Energy/technical data | - Charge efficiency [%] | pct. |  | G, M |  | ctrl | 2018 | 99
162 Flywheels | Technology | Energy/technical data | - Discharge efficiency [%] | pct. |  | G, M |  | ctrl | 2018 | 99
162 Flywheels | Technology | Energy/technical data | Application |  |  |  |  | ctrl | 2018 | System
162 Flywheels | Technology | Energy/technical data | Auxiliary electricity consumption [% of output] | pct. |  | C |  | ctrl | 2018 | 0
162 Flywheels | Technology | Energy/technical data | Construction time [years] | years |  | A, M |  | ctrl | 2018 | 0.5
162 Flywheels | Technology | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | H | [16] | ctrl | 2018 | 5
162 Flywheels | Technology | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A, F, M |  | ctrl | 2018 | 0.1
162 Flywheels | Technology | Energy/technical data | Forced outage [%] | pct. |  |  | [17] | ctrl | 2018 | 0
162 Flywheels | Technology | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2018 | Mechanical
162 Flywheels | Technology | Energy/technical data | Input capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2018 | 1
162 Flywheels | Technology | Energy/technical data | Output capacity for one unit [MW] | MW |  | A, F, M |  | ctrl | 2018 | 1
162 Flywheels | Technology | Energy/technical data | Planned outage [weeks/year] | weeks/year |  |  |  | ctrl | 2018 | 0
162 Flywheels | Technology | Energy/technical data | Round trip efficiency [%] | pct. |  | G, M |  | ctrl | 2018 | 98
162 Flywheels | Technology | Energy/technical data | Technical lifetime [years] | years |  | B, M | [17] | ctrl | 2018 | 20
162 Flywheels | Technology | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | D |  | ctrl | 2018 | 0.10634
162 Flywheels | Technology | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | D |  | ctrl | 2018 | 1.0634
162 Flywheels | Technology | Financial data | Fixed O&M [€/MW/year] | EUR/MW/year | 2020 | D, M |  | ctrl | 2018 | 797.55
162 Flywheels | Technology | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | E, J, L | [18] | ctrl | 2018 | 1.0634
162 Flywheels | Technology | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | I | [7] | ctrl | 2018 | 0
162 Flywheels | Technology | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2018 | 0.003
162 Flywheels | Technology | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | D, M |  | ctrl | 2018 | 0.003
162 Flywheels | Technology | Technology-specific data | Cycle life |  |  | A |  | ctrl | 2018 | 106
162 Flywheels | Technology | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A |  | ctrl | 2018 | 115
162 Flywheels | Technology | Technology-specific data | Specific energy [Wh/l] | Wh/l |  | A |  | ctrl | 2018 | 500
162 Flywheels | Technology | Technology-specific data | Specific investment [M€/MW] | MEUR/MW | 2020 | A | [18] | ctrl | 2018 | 0.1744
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | Lower | 2020 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | Lower | 2050 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | Upper | 2020 | 98.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | Upper | 2050 | 99
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | ctrl | 2015 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | ctrl | 2020 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | ctrl | 2030 | 98.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | ctrl | 2040 | 98.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Charge efficiency [%] | pct. |  | D | [2] | ctrl | 2050 | 98.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | Lower | 2020 | 97
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | Lower | 2050 | 97
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | Upper | 2020 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | Upper | 2050 | 98
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | ctrl | 2015 | 97
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | ctrl | 2020 | 97
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | ctrl | 2030 | 97.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | ctrl | 2040 | 97.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | - Discharge efficiency [%] | pct. |  | D | [2] | ctrl | 2050 | 97.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | ctrl | 2040 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System, power- and energy-intensive
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | Lower | 2020 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | Lower | 2050 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | Upper | 2020 | 0.25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | Upper | 2050 | 0.25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | ctrl | 2015 | 0.25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | ctrl | 2020 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | ctrl | 2030 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | ctrl | 2040 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Construction time [years] | years |  |  | [38] | ctrl | 2050 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | Lower | 2020 | 0.05
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | Lower | 2050 | 0.05
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | Upper | 2020 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | Upper | 2050 | 0.15
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | ctrl | 2015 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | ctrl | 2020 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | ctrl | 2030 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | ctrl | 2040 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E | [18,50,52] | ctrl | 2050 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | Lower | 2020 | 5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | Lower | 2050 | 7
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | Upper | 2020 | 9
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | Upper | 2050 | 12
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | ctrl | 2015 | 3.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | ctrl | 2020 | 6
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | ctrl | 2030 | 7
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | ctrl | 2040 | 8
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A | [2,14] | ctrl | 2050 | 8
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | Lower | 2020 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | Lower | 2050 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | Upper | 2020 | 0.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | Upper | 2050 | 0.3
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | ctrl | 2015 | 0.4
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | ctrl | 2020 | 0.38
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | ctrl | 2030 | 0.35
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | ctrl | 2040 | 0.3
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Forced outage [%] | pct. |  | F |  | ctrl | 2050 | 0.25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2040 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Electricity
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | Lower | 2020 | 2.7
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | Lower | 2050 | 3.7
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | Upper | 2020 | 3.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | Upper | 2050 | 4.7
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2015 | 1.6
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2020 | 3
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2030 | 3.5
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2040 | 4
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2050 | 4
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | Lower | 2020 | 16
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | Lower | 2050 | 22
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | Upper | 2020 | 21
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | Upper | 2050 | 28
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2015 | 9.6
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2020 | 18
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2030 | 21
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2040 | 24
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B | [2,14] | ctrl | 2050 | 24
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | Lower | 2020 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | Lower | 2050 | 0.05
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | Upper | 2020 | 0.25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | Upper | 2050 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | ctrl | 2015 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | ctrl | 2020 | 0.2
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | ctrl | 2030 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | ctrl | 2040 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F |  | ctrl | 2050 | 0.1
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | Lower | 2020 | 90
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | Lower | 2050 | 91
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | Upper | 2020 | 92
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | Upper | 2050 | 94
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | ctrl | 2015 | 91
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | ctrl | 2020 | 91
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | ctrl | 2030 | 92
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | ctrl | 2040 | 92
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] AC | pct. |  | C | [3,21,22,51] | ctrl | 2050 | 92
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | Lower | 2020 | 95
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | Lower | 2050 | 95
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | Upper | 2020 | 96
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | Upper | 2050 | 97
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | ctrl | 2015 | 95
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | ctrl | 2020 | 95
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | ctrl | 2030 | 96
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | ctrl | 2040 | 96
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Round trip efficiency [%] DC | pct. |  | C | [3,21,22,51] | ctrl | 2050 | 96
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | Lower | 2020 | 15
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | Lower | 2050 | 20
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | Upper | 2020 | 25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | Upper | 2050 | 45
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | ctrl | 2015 | 15
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | ctrl | 2020 | 20
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | ctrl | 2030 | 25
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | ctrl | 2040 | 30
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Energy/technical data | Technical lifetime [years] | years |  | G | [3,5,8,14] | ctrl | 2050 | 30
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | Lower | 2020 | 0.25522
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | Lower | 2050 | 0.042536
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | Upper | 2020 | 0.54233
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | Upper | 2050 | 0.26585
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | ctrl | 2015 | 0.30839
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | ctrl | 2020 | 0.28712
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | ctrl | 2030 | 0.17014
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | ctrl | 2040 | 0.10634
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - capacity component [M€/MW] PCS | MEUR/MW | 2020 | K | [54–56] | ctrl | 2050 | 0.063804
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | Lower | 2020 | 0.074438
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | Lower | 2050 | 0.027648
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | Upper | 2020 | 0.20098
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | Upper | 2050 | 0.12229
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | ctrl | 2015 | 0.32753
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | ctrl | 2020 | 0.14037
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | ctrl | 2030 | 0.065931
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | ctrl | 2040 | 0.04679
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | J | [44] | ctrl | 2050 | 0.037219
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | Lower | 2020 | 0.095706
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | Lower | 2050 | 0.021268
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | Upper | 2020 | 0.11697
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | Upper | 2050 | 0.11697
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | ctrl | 2015 | 0.11697
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | ctrl | 2020 | 0.10634
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | ctrl | 2030 | 0.085072
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | ctrl | 2040 | 0.05317
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | L | [22,40,54] | ctrl | 2050 | 0.042536
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | Lower | 2020 | 0.47853
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | Lower | 2050 | 0.42536
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | Upper | 2020 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | Upper | 2050 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | ctrl | 2015 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | ctrl | 2020 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | ctrl | 2030 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | ctrl | 2040 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Fixed O&M [k€/MW/year] | kEUR/MW/year | 2020 | M | [22] | ctrl | 2050 | 0.57424
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | Lower | 2020 | 0.93579
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | Lower | 2050 | 0.17652
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | Upper | 2020 | 1.945
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | Upper | 2050 | 1.0368
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | ctrl | 2015 | 1.3697
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | ctrl | 2020 | 1.1081
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | ctrl | 2030 | 0.66143
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | ctrl | 2040 | 0.41898
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I | [44,48] | ctrl | 2050 | 0.27117
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | Lower | 2020 | 0.42536
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | Lower | 2050 | 0.31902
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | Upper | 2020 | 5.955
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | Upper | 2050 | 2.6585
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | ctrl | 2015 | 2.2331
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | ctrl | 2020 | 2.1268
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | ctrl | 2030 | 1.9141
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | ctrl | 2040 | 1.8078
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [55] | ctrl | 2050 | 1.7014
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | Lower | 2020 | 0
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | Lower | 2050 | 0
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | Upper | 2020 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | Upper | 2050 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2015 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2020 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2030 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2040 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2050 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | Lower | 2020 | 0
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | Lower | 2050 | 0
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | Upper | 2020 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | Upper | 2050 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2015 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2020 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2030 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2040 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [53] | ctrl | 2050 | 0.08
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | Lower | 2020 | 0.29775
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | Lower | 2050 | 0.05317
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | Upper | 2020 | 0.61677
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | Upper | 2050 | 0.32965
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | ctrl | 2015 | 0.41473
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | ctrl | 2020 | 0.35092
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | ctrl | 2030 | 0.21268
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | ctrl | 2040 | 0.12761
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | Q | [41,44,48,54–56] | ctrl | 2050 | 0.085072
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | Lower | 2020 | 150
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | Lower | 2050 | 200
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | Upper | 2020 | 200
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | Upper | 2050 | 400
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | ctrl | 2015 | 118
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | ctrl | 2020 | 130
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | ctrl | 2030 | 173
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | ctrl | 2040 | 216
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy density [kWh/m3] | kWh/m3 |  | S | [2,24] | ctrl | 2050 | 260
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | Lower | 2020 | 0.17014
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | Lower | 2050 | 0.048916
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | Upper | 2020 | 0.27542
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | Upper | 2050 | 0.18716
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | ctrl | 2015 | 0.4445
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | ctrl | 2020 | 0.24671
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | ctrl | 2030 | 0.151
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | ctrl | 2040 | 0.09996
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Energy storage expansion cost [M€/MWh] | MEUR/MWh | 2020 | O | [44,48] | ctrl | 2050 | 0.079755
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | Lower | 2020 | 10000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | Lower | 2050 | 20000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | Upper | 2020 | 16000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | Upper | 2050 | 70000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | ctrl | 2015 | 6000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | ctrl | 2020 | 14000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | ctrl | 2030 | 30000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | ctrl | 2040 | 40000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Lifetime in total number of cycles |  |  | R | [3–5,14] | ctrl | 2050 | 50000
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | Lower | 2020 | 0.25522
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | Lower | 2050 | 0.042536
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | Upper | 2020 | 0.54233
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | Upper | 2050 | 0.26585
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | ctrl | 2015 | 0.30839
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | ctrl | 2020 | 0.28712
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | ctrl | 2030 | 0.17014
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | ctrl | 2040 | 0.10634
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Output capacity expansion cost [M€/MW] | MEUR/MW | 2020 | P | [54–56] | ctrl | 2050 | 0.063804
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | Lower | 2020 | 450
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | Lower | 2050 | 600
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | Upper | 2020 | 600
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | Upper | 2050 | 1200
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | ctrl | 2015 | 354
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | ctrl | 2020 | 390
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | ctrl | 2030 | 519
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | ctrl | 2040 | 648
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Power density [kW/m3] | kW/m3 |  | S | [2,24] | ctrl | 2050 | 780
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | Lower | 2020 | 100
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | Lower | 2050 | 150
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | Upper | 2020 | 140
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | Upper | 2050 | 300
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | ctrl | 2015 | 95
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | ctrl | 2020 | 105
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | ctrl | 2030 | 139
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | ctrl | 2040 | 174
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | S | [2,24] | ctrl | 2050 | 209
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | Lower | 2020 | 300
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | Lower | 2050 | 450
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | Upper | 2020 | 420
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | Upper | 2050 | 900
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | ctrl | 2015 | 285
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | ctrl | 2020 | 315
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | ctrl | 2030 | 417
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | ctrl | 2040 | 522
180 Lithium Ion Battery | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135) | Technology-specific data | Specific power [W/kg] | W/kg |  | S | [2,24] | ctrl | 2050 | 627
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System, power- and energy-intensive
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | Lower | 2020 | 0.2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | Lower | 2050 | 0.2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | Upper | 2020 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | Upper | 2050 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | ctrl | 2015 | 1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | ctrl | 2020 | 1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | ctrl | 2030 | 1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Construction time [years] | years |  | E,M | [9] | ctrl | 2050 | 1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | Lower | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | Lower | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | Upper | 2020 | 0.2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | Upper | 2050 | 0.2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | ctrl | 2015 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | ctrl | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | ctrl | 2030 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | C | [4];[22] | ctrl | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | Lower | 2020 | 0.4
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | Lower | 2050 | 0.4
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | Upper | 2020 | 800
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | Upper | 2050 | 800
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | ctrl | 2015 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | ctrl | 2020 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | ctrl | 2030 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,M | [4]+[9] | ctrl | 2050 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | Lower | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | Lower | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | Upper | 2020 | 5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | Upper | 2050 | 5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | ctrl | 2015 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | ctrl | 2020 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | ctrl | 2030 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Forced outage [%] | pct. |  | D,M | [1] | ctrl | 2050 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Electricity
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | Lower | 2020 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | Lower | 2050 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | Upper | 2020 | 200
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | Upper | 2050 | 200
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2015 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2020 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2030 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2050 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | Lower | 2020 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | Lower | 2050 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | Upper | 2020 | 200
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | Upper | 2050 | 200
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2015 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2020 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2030 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,M | [4] | ctrl | 2050 | 0.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | Lower | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | Lower | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | Upper | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | Upper | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | ctrl | 2015 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | ctrl | 2020 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | ctrl | 2030 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | D,M | [1] | ctrl | 2050 | 0
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | Lower | 2020 | 62
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | Lower | 2050 | 67
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | Upper | 2020 | 88
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | Upper | 2050 | 95
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | ctrl | 2015 | 78
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | ctrl | 2020 | 78
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | ctrl | 2030 | 78
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Round trip efficiency DC [%] | pct. |  | B | [5];[22] | ctrl | 2050 | 78
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | Lower | 2020 | 6
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | Lower | 2050 | 8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | Upper | 2020 | 23
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | Upper | 2050 | 32
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | ctrl | 2015 | 20
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | ctrl | 2020 | 20
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | ctrl | 2030 | 20
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Energy/technical data | Technical lifetime [years] | years |  |  | [4];[28]+[22] | ctrl | 2050 | 20
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | Lower | 2020 | 0.45726
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | Lower | 2050 | 0.37219
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | Upper | 2020 | 0.51043
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | Upper | 2050 | 0.41473
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | ctrl | 2015 | 0.47853
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | ctrl | 2020 | 0.43599
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | ctrl | 2030 | 0.35092
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | H | [22]+[25]+[27]/[19] | ctrl | 2050 | 0.35092
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | Lower | 2020 | 0.40409
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | Lower | 2050 | 0.20205
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | Upper | 2020 | 0.9996
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | Upper | 2050 | 0.4679
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | ctrl | 2015 | 0.61677
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | ctrl | 2020 | 0.47853
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | ctrl | 2030 | 0.25522
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | H, I | [22]+[27] | ctrl | 2050 | 0.23395
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | Lower | 2020 | 0.042536
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | Lower | 2050 | 0.021268
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | Upper | 2020 | 0.095706
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | Upper | 2050 | 0.05317
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | ctrl | 2015 | 0.063804
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | ctrl | 2020 | 0.05317
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | ctrl | 2030 | 0.031902
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | J | [19] | ctrl | 2050 | 0.031902
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | Lower | 2020 | 0.8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | Lower | 2050 | 0.6
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | Upper | 2020 | 4.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | Upper | 2050 | 3.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | ctrl | 2015 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | ctrl | 2020 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | ctrl | 2030 | 1.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Fixed O&M [% total investment] | pct.investment |  |  | [24]+[25]/[2] | ctrl | 2050 | 1.5
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | Lower | 2020 | 0.5636
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | Lower | 2050 | 0.31902
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | Upper | 2020 | 1.2229
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | Upper | 2050 | 0.61677
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | ctrl | 2015 | 0.79755
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | ctrl | 2020 | 0.63804
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | ctrl | 2030 | 0.37219
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | H | [22]+[27]/[19] | ctrl | 2050 | 0.35092
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | Lower | 2020 | 0.21268
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | Lower | 2050 | 0.21268
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | Upper | 2020 | 2.9775
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | Upper | 2050 | 2.9775
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | ctrl | 2015 | 0.95706
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | ctrl | 2020 | 0.95706
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | ctrl | 2030 | 0.95706
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | 0 | [25]/[2] | ctrl | 2050 | 0.95706
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | Lower | 2020 | 0.004
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | Lower | 2050 | 0.004
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | Upper | 2020 | 1.4
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | Upper | 2050 | 1.4
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | ctrl | 2015 | 0.07
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | ctrl | 2020 | 0.07
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | ctrl | 2030 | 0.07
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | F,G,M | [1] | ctrl | 2050 | 0.07
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | Lower | 2020 | 0.005
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | Lower | 2050 | 0.005
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | Upper | 2020 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | Upper | 2050 | 2
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | ctrl | 2015 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | ctrl | 2020 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | ctrl | 2030 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | F,G | [4]+[30] | ctrl | 2050 | 0.1
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | Lower | 2020 | 2.2331
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | Lower | 2050 | 1.2761
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | Upper | 2020 | 4.8916
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | Upper | 2050 | 2.4458
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | ctrl | 2015 | 3.1902
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | ctrl | 2020 | 2.5522
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | ctrl | 2030 | 1.4888
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | H | [22]+[31]+[27]/[19] | ctrl | 2050 | 1.3824
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | Lower | 2020 | 4520
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | Lower | 2050 | 4520
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | Upper | 2020 | 11300
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | Upper | 2050 | 11300
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | ctrl | 2015 | 9040
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | ctrl | 2020 | 9040
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | ctrl | 2030 | 9040
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | A,L,M | [4] | ctrl | 2050 | 9040
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | Lower | 2020 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | Lower | 2050 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | Upper | 2020 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | Upper | 2050 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | ctrl | 2015 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | ctrl | 2020 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | ctrl | 2030 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Lifetime in total number of cycles |  |  | K | [1] | ctrl | 2050 | -¦-
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | Lower | 2020 | 1130
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | Lower | 2050 | 1130
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | Upper | 2020 | 2825
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | Upper | 2050 | 2825
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | ctrl | 2015 | 2260
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | ctrl | 2020 | 2260
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | ctrl | 2030 | 2260
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Power density [W/m3] | W/m3 |  | A,L,M | [4] | ctrl | 2050 | 2260
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | Lower | 2020 | 5.9
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | Lower | 2050 | 5.9
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | Upper | 2020 | 14.75
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | Upper | 2050 | 14.75
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | ctrl | 2015 | 11.8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | ctrl | 2020 | 11.8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | ctrl | 2030 | 11.8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | A,L,M | [4] | ctrl | 2050 | 11.8
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | Lower | 2020 | 1.45
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | Lower | 2050 | 1.45
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | Upper | 2020 | 3.63
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | Upper | 2050 | 3.63
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | ctrl | 2015 | 2.9
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | ctrl | 2020 | 2.9
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | ctrl | 2030 | 2.9
181 Vanadium Redox Flow Battery | Vanadium Redox Battery (VRB) | Technology-specific data | Specific power [W/kg] | W/kg |  | A,L,M | [4] | ctrl | 2050 | 2.9
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
182 Na-S Battery | NaS battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | Lower | 2020 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | Lower | 2050 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | Upper | 2020 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | Upper | 2050 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System, power- and energy-intensive
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | Lower | 2020 | 0.2
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | Lower | 2050 | 0.2
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | Upper | 2020 | 2
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | Upper | 2050 | 2
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | ctrl | 2020 | 0.5
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | ctrl | 2030 | 0.5
182 Na-S Battery | NaS battery | Energy/technical data | Construction time [years] | years |  | Q | [1] | ctrl | 2050 | 0.5
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | Lower | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | Lower | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | Upper | 2020 | 1
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | Upper | 2050 | 1
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | ctrl | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | ctrl | 2030 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | ctrl | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | Lower | 2020 | 30
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | Lower | 2050 | 30
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | Upper | 2020 | 3000
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | Upper | 2050 | 3000
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | ctrl | 2020 | 300
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | ctrl | 2030 | 300
182 Na-S Battery | NaS battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | ctrl | 2050 | 300
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | Lower | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | Lower | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | Upper | 2020 | 2
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | Upper | 2050 | 2
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | ctrl | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | ctrl | 2030 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | ctrl | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Electricity
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | Lower | 2020 | 5
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | Lower | 2050 | 5
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | Upper | 2020 | 500
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | Upper | 2050 | 500
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2020 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2030 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2050 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | Lower | 2020 | 5
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | Lower | 2050 | 5
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | Upper | 2020 | 500
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | Upper | 2050 | 500
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2020 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2030 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2050 | 50
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | Lower | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | Lower | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | Upper | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | Upper | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | ctrl | 2020 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | ctrl | 2030 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | ctrl | 2050 | 0
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | Lower | 2020 | 71
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | Lower | 2050 | 74
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | Upper | 2020 | 92
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | Upper | 2050 | 96
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | ctrl | 2020 | 83
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | ctrl | 2030 | 85
182 Na-S Battery | NaS battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | ctrl | 2050 | 85
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | Lower | 2020 | 10
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | Lower | 2050 | 14
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | Upper | 2020 | 28
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | Upper | 2050 | 36
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | ctrl | 2020 | 19
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | ctrl | 2030 | 24
182 Na-S Battery | NaS battery | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | ctrl | 2050 | 24
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | Lower | 2020 | 0.23395
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | Lower | 2050 | 0.19141
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | Upper | 2020 | 0.82945
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | Upper | 2050 | 0.68058
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | ctrl | 2020 | 0.43599
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | ctrl | 2030 | 0.35092
182 Na-S Battery | NaS battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | ctrl | 2050 | 0.35092
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | Lower | 2020 | 0.19141
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | Lower | 2050 | 0.085072
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | Upper | 2020 | 0.5317
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | Upper | 2050 | 0.24458
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | ctrl | 2020 | 0.26585
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | ctrl | 2030 | 0.14888
182 Na-S Battery | NaS battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | ctrl | 2050 | 0.11697
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | Lower | 2020 | 0.042536
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | Lower | 2050 | 0.021268
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | Upper | 2020 | 0.10634
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | Upper | 2050 | 0.05317
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | ctrl | 2020 | 0.05317
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | ctrl | 2030 | 0.031902
182 Na-S Battery | NaS battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | ctrl | 2050 | 0.031902
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | Lower | 2020 | 0.8
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | Lower | 2050 | 0.8
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | Upper | 2020 | 7.2
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | Upper | 2050 | 7.2
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | ctrl | 2020 | 1.5
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | ctrl | 2030 | 1.5
182 Na-S Battery | NaS battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | ctrl | 2050 | 1.5
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | Lower | 2020 | 0.26585
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | Lower | 2050 | 0.13824
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | Upper | 2020 | 0.77628
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | Upper | 2050 | 0.41473
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | ctrl | 2020 | 0.39346
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | ctrl | 2030 | 0.24458
182 Na-S Battery | NaS battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | ctrl | 2050 | 0.21268
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | Lower | 2020 | 0.31902
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | Lower | 2050 | 0.31902
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | Upper | 2020 | 5.955
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | Upper | 2050 | 5.955
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | ctrl | 2020 | 1.9141
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | ctrl | 2030 | 1.9141
182 Na-S Battery | NaS battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | ctrl | 2050 | 1.9141
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | Lower | 2020 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | Lower | 2050 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | Upper | 2020 | 0.05
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | Upper | 2050 | 0.05
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | ctrl | 2020 | 0.05
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | ctrl | 2030 | 0.05
182 Na-S Battery | NaS battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | ctrl | 2050 | 0.05
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | Lower | 2020 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | Lower | 2050 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | Upper | 2020 | 0.02
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | Upper | 2050 | 0.02
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | ctrl | 2020 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | ctrl | 2030 | 0.001
182 Na-S Battery | NaS battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | ctrl | 2050 | 0.001
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | Lower | 2020 | 1.5951
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | Lower | 2050 | 0.85072
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | Upper | 2020 | 4.679
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | Upper | 2050 | 2.4458
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | ctrl | 2020 | 2.3395
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | ctrl | 2030 | 1.4888
182 Na-S Battery | NaS battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | ctrl | 2050 | 1.2761
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | Lower | 2020 | 19500
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | Lower | 2050 | 19500
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | Upper | 2020 | 32500
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | Upper | 2050 | 32500
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | ctrl | 2020 | 26000
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | ctrl | 2030 | 26000
182 Na-S Battery | NaS battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | ctrl | 2050 | 26000
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | Lower | 2020 | 1100
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | Lower | 2050 | 1500
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | Upper | 2020 | 11200
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | Upper | 2050 | 15000
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | ctrl | 2020 | 5600
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | ctrl | 2030 | 7500
182 Na-S Battery | NaS battery | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | ctrl | 2050 | 7500
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | Lower | 2020 | 3225
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | Lower | 2050 | 3225
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | Upper | 2020 | 5375
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | Upper | 2050 | 5375
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | ctrl | 2020 | 4300
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | ctrl | 2030 | 4300
182 Na-S Battery | NaS battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | ctrl | 2050 | 4.3
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | Lower | 2020 | 42
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | Lower | 2050 | 42
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | Upper | 2020 | 70
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | Upper | 2050 | 70
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | ctrl | 2020 | 56
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | ctrl | 2030 | 56
182 Na-S Battery | NaS battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | ctrl | 2050 | 56
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | Lower | 2020 | 6.98
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | Lower | 2050 | 6.98
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | Upper | 2020 | 11.63
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | Upper | 2050 | 11.63
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | ctrl | 2020 | 9.3
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | ctrl | 2030 | 9.3
182 Na-S Battery | NaS battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | ctrl | 2050 | 9.3
182 Na-S Battery | Technology | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
182 Na-S Battery | Technology | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
182 Na-S Battery | Technology | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System, power- and energy-intensive
182 Na-S Battery | Technology | Energy/technical data | Construction time [years] | years |  | Q | [1] | ctrl | 2015 | 0.5
182 Na-S Battery | Technology | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | D,Q | [11]/[30]/[26] | ctrl | 2015 | 0
182 Na-S Battery | Technology | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A B,Q | [9] | ctrl | 2015 | 250
182 Na-S Battery | Technology | Energy/technical data | Forced outage [%] | pct. |  | E,Q | [13] | ctrl | 2015 | 0
182 Na-S Battery | Technology | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Electricity
182 Na-S Battery | Technology | Energy/technical data | Input capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2015 | 35
182 Na-S Battery | Technology | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,Q | [9] | ctrl | 2015 | 35
182 Na-S Battery | Technology | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,Q | [13] | ctrl | 2015 | 0
182 Na-S Battery | Technology | Energy/technical data | Round trip efficiency DC [%] | pct. |  | C | [9];[26] | ctrl | 2015 | 83
182 Na-S Battery | Technology | Energy/technical data | Technical lifetime [years] | years |  | G | [13];[25]+[27] | ctrl | 2015 | 15
182 Na-S Battery | Technology | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | G, K | [22]+[26] | ctrl | 2015 | 0.66994
182 Na-S Battery | Technology | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | G, J | [22]+[26] | ctrl | 2015 | 0.32965
182 Na-S Battery | Technology | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | G | [22]+[26] | ctrl | 2015 | 0.063804
182 Na-S Battery | Technology | Financial data | Fixed O&M [% total investment] | pct.investment |  | G,L,M | [23];[24] | ctrl | 2015 | 1.5
182 Na-S Battery | Technology | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | G | [22];[25]+[26] | ctrl | 2015 | 0.48916
182 Na-S Battery | Technology | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | G | [24]+[23] | ctrl | 2015 | 1.9141
182 Na-S Battery | Technology | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,I,Q | [9] | ctrl | 2015 | 0.05
182 Na-S Battery | Technology | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  | H | [10]+[28] | ctrl | 2015 | 0.001
182 Na-S Battery | Technology | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | G | [22];[25]+[26] | ctrl | 2015 | 3.5092
182 Na-S Battery | Technology | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P,Q |  | ctrl | 2015 | 26000
182 Na-S Battery | Technology | Technology-specific data | Lifetime in total number of cycles |  |  | N, G | [9];[25]+[27] | ctrl | 2015 | 4500
182 Na-S Battery | Technology | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P,Q | [10] | ctrl | 2015 | 4300
182 Na-S Battery | Technology | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P,Q | [10] | ctrl | 2015 | 56
182 Na-S Battery | Technology | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P,Q | [10] | ctrl | 2015 | 9.3
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Charge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Lower | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | Upper | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2015 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2020 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2030 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | - Discharge efficiency [%] | pct. |  |  |  | ctrl | 2050 | -
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Application |  |  |  |  | ctrl | 2015 | System, power- and energy-intensive
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Application |  |  |  |  | ctrl | 2020 | System, power- and energy-intensive
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Application |  |  |  |  | ctrl | 2030 | System, power- and energy-intensive
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Application |  |  |  |  | ctrl | 2050 | System, power- and energy-intensive
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | Lower | 2020 | 0.2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | Lower | 2050 | 0.2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | Upper | 2020 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | Upper | 2050 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | ctrl | 2015 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | ctrl | 2020 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | ctrl | 2030 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Construction time [years] | years |  | G,P | [11] | ctrl | 2050 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | Lower | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | Lower | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | Upper | 2020 | 15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | Upper | 2050 | 15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | ctrl | 2015 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | ctrl | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | ctrl | 2030 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy losses during storage [%/day] | pct./day |  | E,P | [35]+[5];[31] | ctrl | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | Lower | 2020 | 3.11
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | Lower | 2050 | 3.11
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | Upper | 2020 | 5.19
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | Upper | 2050 | 5.19
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | ctrl | 2015 | 4.43
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | ctrl | 2020 | 4.15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | ctrl | 2030 | 4.15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Energy storage capacity for one unit [MWh] | MWh |  | A,B,P | [12]+[11] | ctrl | 2050 | 4.15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | Lower | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | Lower | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | Upper | 2020 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | Upper | 2050 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | ctrl | 2015 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | ctrl | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | ctrl | 2030 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Forced outage [%] | pct. |  | F,P | [8] | ctrl | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2020 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | Lower | 2050 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2020 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | Upper | 2050 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2015 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2020 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2030 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Form of energy stored |  |  |  |  | ctrl | 2050 | Electricity
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | Lower | 2020 | 0.34
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | Lower | 2050 | 0.34
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | Upper | 2020 | 0.56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | Upper | 2050 | 0.56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | ctrl | 2015 | 0.42
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | ctrl | 2020 | 0.45
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | ctrl | 2030 | 0.45
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Input capacity for one unit [MW] | MW |  | C,P | [34]+[8] | ctrl | 2050 | 0.45
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | Lower | 2020 | 0.9
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | Lower | 2050 | 0.9
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | Upper | 2020 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | Upper | 2050 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | ctrl | 2015 | 1.13
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | ctrl | 2020 | 1.2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | ctrl | 2030 | 1.2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Output capacity for one unit [MW] | MW |  | A,B,P | [12]+[11] | ctrl | 2050 | 1.2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | Lower | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | Lower | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | Upper | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | Upper | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | ctrl | 2015 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | ctrl | 2020 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | ctrl | 2030 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Planned outage [weeks/year] | weeks/year |  | F,P | [8] | ctrl | 2050 | 0
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | Lower | 2020 | 81
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | Lower | 2050 | 83
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | Upper | 2020 | 93
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | Upper | 2050 | 95
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | ctrl | 2015 | 87
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | ctrl | 2020 | 87
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | ctrl | 2030 | 87
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Round trip efficiency DC [%] | pct. |  | D | [4]+[7]; [31] | ctrl | 2050 | 87
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | Lower | 2020 | 9
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | Lower | 2050 | 12
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | Upper | 2020 | 25
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | Upper | 2050 | 33
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | ctrl | 2015 | 15
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | ctrl | 2020 | 17
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | ctrl | 2030 | 23
183 Na-NiCl2 Battery | Na-NiCl2 battery | Energy/technical data | Technical lifetime [years] | years |  |  | [28]+[8];[30]+[32]+[31] | ctrl | 2050 | 23
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | Lower | 2020 | 0.31902
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | Lower | 2050 | 0.26585
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | Upper | 2020 | 0.61677
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | Upper | 2050 | 0.4998
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | ctrl | 2015 | 0.51043
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | ctrl | 2020 | 0.43599
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | ctrl | 2030 | 0.35092
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - capacity component [M€/MW] | MEUR/MW | 2020 | L | [12]; [31] | ctrl | 2050 | 0.35092
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | Lower | 2020 | 0.22331
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | Lower | 2050 | 0.095706
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | Upper | 2020 | 0.34029
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | Upper | 2050 | 0.14888
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | ctrl | 2015 | 0.80818
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | ctrl | 2020 | 0.27648
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | ctrl | 2030 | 0.14888
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - energy component [M€/MWh] | MEUR/MWh | 2020 | K | [12]; [31] | ctrl | 2050 | 0.11697
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | Lower | 2020 | 0.031902
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | Lower | 2050 | 0.010634
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | Upper | 2020 | 0.042536
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | Upper | 2050 | 0.021268
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | ctrl | 2015 | 0.085072
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | ctrl | 2020 | 0.031902
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | ctrl | 2030 | 0.021268
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | - other project costs [M€/MWh] | MEUR/MWh | 2020 | 0 | [12] | ctrl | 2050 | 0.021268
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | Lower | 2020 | 0.9
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | Lower | 2050 | 0.9
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | Upper | 2020 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | Upper | 2050 | 2
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | ctrl | 2015 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | ctrl | 2020 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | ctrl | 2030 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Fixed O&M [% total investment] | pct.investment |  | M | [29]+[28]+[27] | ctrl | 2050 | 1.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | Lower | 2020 | 0.34029
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | Lower | 2050 | 0.19141
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | Upper | 2020 | 0.5636
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | Upper | 2050 | 0.31902
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | ctrl | 2015 | 1.0634
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | ctrl | 2020 | 0.44663
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | ctrl | 2030 | 0.27648
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Specific investment [M€/MWh] | MEUR/MWh | 2020 | I, J | [12]+[28]; [30]+[31] | ctrl | 2050 | 0.24458
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | Lower | 2020 | 0.42536
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | Lower | 2050 | 0.42536
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | Upper | 2020 | 2.2331
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | Upper | 2050 | 2.2331
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | ctrl | 2015 | 0.63804
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | ctrl | 2020 | 0.63804
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | ctrl | 2030 | 0.63804
183 Na-NiCl2 Battery | Na-NiCl2 battery | Financial data | Variable O&M [€/MWh] | EUR/MWh | 2020 | N | [29] | ctrl | 2050 | 0.63804
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | Lower | 2020 | 0.001
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | Lower | 2050 | 0.001
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | Upper | 2020 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | Upper | 2050 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | ctrl | 2015 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | ctrl | 2020 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | ctrl | 2030 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from full-rated charge to full-rated discharge [sec] | sec |  | H,P | [4] | ctrl | 2050 | 0.5
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | Lower | 2020 | 0.001
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | Lower | 2050 | 0.001
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | Upper | 2020 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | Upper | 2050 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | ctrl | 2015 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | ctrl | 2020 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | ctrl | 2030 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Regulation ability | Response time from idle to full-rated discharge [sec] | sec |  |  | [10]/[4]+[33] | ctrl | 2050 | 0.02
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | Lower | 2020 | 1.1697
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | Lower | 2050 | 0.63804
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | Upper | 2020 | 1.9141
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | Upper | 2050 | 1.0634
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | ctrl | 2015 | 3.1902
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | ctrl | 2020 | 1.4888
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | ctrl | 2030 | 0.95706
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Alternative Investment cost [M€/MW] | MEUR/MW | 2020 | I | [12]+[28] | ctrl | 2050 | 0.85072
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | Lower | 2020 | 24525
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | Lower | 2050 | 24525
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | Upper | 2020 | 40875
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | Upper | 2050 | 40875
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | ctrl | 2015 | 32700
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | ctrl | 2020 | 32700
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | ctrl | 2030 | 32700
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Energy density [Wh/m3] | Wh/m3 |  | O,P | [3] | ctrl | 2050 | 32700
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | Lower | 2020 | 1500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | Lower | 2050 | 1500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | Upper | 2020 | 11300
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | Upper | 2050 | 11300
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | ctrl | 2015 | 4500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | ctrl | 2020 | 4500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | ctrl | 2030 | 4500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Lifetime in total number of cycles |  |  | O | [4]+[8];[30]+[32] | ctrl | 2050 | 4500
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | Lower | 2020 | 7012
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | Lower | 2050 | 7012
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | Upper | 2020 | 11687
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | Upper | 2050 | 11687
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | ctrl | 2015 | 9350
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | ctrl | 2020 | 9350
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | ctrl | 2030 | 9350
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Power density [W/m3] | W/m3 |  | O,P | [8] | ctrl | 2050 | 9350
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | Lower | 2020 | 42
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | Lower | 2050 | 42
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | Upper | 2020 | 70
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | Upper | 2050 | 70
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | ctrl | 2015 | 56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | ctrl | 2020 | 56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | ctrl | 2030 | 56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific energy [Wh/kg] | Wh/kg |  | O,P | [3] | ctrl | 2050 | 56
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | Lower | 2020 | 12
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | Lower | 2050 | 12
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | Upper | 2020 | 20
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | Upper | 2050 | 20
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | ctrl | 2015 | 16
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | ctrl | 2020 | 16
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | ctrl | 2030 | 16
183 Na-NiCl2 Battery | Na-NiCl2 battery | Technology-specific data | Specific power [W/kg] | W/kg |  | O,P | [8] | ctrl | 2050 | 16

## Notes
ws | description
140 PTES seasonal | A. The charge/discharge capacity corresponds to an example where a solar fraction of 40 % was desired. Other input/output capacities [also relative to storage capacity) may occur for other purposes. Measurements from SUNSTORE 3 show approx. 80 % efficiency for a storage with heat pump.
140 PTES seasonal | B. Values in the table are without a heat pump. The storage loss depends on several parameters, such as store volume, insulation, whether a heat pump is part of the system etc. Round trip efficiency of approx. 80 % when applying a heat pump for cooling to 10°C. [Dis-)charge losses 0 cf. Direct us...
140 PTES seasonal | C. Approx. 100 MWh/year for pumps, at 2,000 fullload hours for the pumps, considering one full cycle
140 PTES seasonal | D. Current max. Technical lifetime for liners.
140 PTES seasonal | E. Excl. Extensive planning phase with possibly Environmental Impact Assessment etc. Careful timing of steps is mandatory, as the steps of excavation, building, installation of liners etc. Can be done within one summer. If not, the construction time expands to approx. 2 years.
140 PTES seasonal | F. Estimated from the cost of the 7 Danish plants, described in the text and due to effects of economy of scale, the total costs of a PTES in 2015 could be described in a formula: Cost [M€] = 0.9 + 2.44*10-5*V , with V being the volume in m3 . Corresponding to 37EUR/m3 at 70,000 m3 and 0.58...
140 PTES seasonal | G. The Fixed O&M is set according to capacity of the Energy Storage specified in the top of the table. Corresponding to approx. 13,000 EUR/storage/year for e.g. divers for inspection, adding of possible leakages and minor fixes.
140 PTES seasonal | H. Cooling to lower temperatures is only possible when a heat pump is used to chill the PTES.
140 PTES seasonal | I. Total efficiency during a one year cycle, including losses during storage period.
140 PTES seasonal | I. Total efficiency during a one year cycle, including losses during storage period.
142 Small scale hot water tank | A. Considering a temperature difference of 30K (hot/cold), cf. DS12897:2016 [8], and 60K for large tanks, typically for solar thermal applications.
142 Small scale hot water tank | B. As tanks are typically connected directly to the hydraulic heating system of a building, there is no loss due to the dis-/charging. The heat loss of the tank will typically be utilised as spatial heating, if the tank is mounted inside the building.
142 Small scale hot water tank | C. Less than 1 % of the stored energy for circulation pumps.
142 Small scale hot water tank | D. Typically limited to replacement of the anode for every 3 years, potentially the control unit or valves and fittings.
142 Small scale hot water tank | E. Primarily limited by the extent to which the system is held corrosion-free (the enamelling is held undamaged).
142 Small scale hot water tank | F. Installation period assessed to be 3-8 hours each for two skilled workers, i.e. the construction site is cleared/prepared, varying by the tank size.
142 Small scale hot water tank | G. CAPEX cf. a stand-alone cabinet-solution, mounted, site-clearance/preparation and removal of existing heating source/storage not included. Cost for fittings etc. approx. 10 % of total CAPEX. Additional investment for electric heater of approx. 100 EUR may be added if necessary.
142 Small scale hot water tank | H. Only variable O&M is electricity consumption for pumps as specified above.
142 Small scale hot water tank | I. Considering a heat loss of 60 W at temperature 65/35°C in the storage and 20°C ambient for the 90 l unit. Considering an idle/discharging cycle of total 4 hours.
142 Small scale hot water tank | J. Round trip efficiency is not applicable for seasonal storage.
142 Small scale hot water tank | K. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2040: 117, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
142 Small scale hot water tank | L. CAPEX is related to storage volume. I.e. an increase of temperature difference in storage yields a lower specific investment/MWh.
142 Small scale hot water tank | L. CAPEX is related to storage volume. I.e. an increase of temperature difference in storage yields a lower specific investment/MWh.
150 Underground Storage of Gas | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
150 Underground Storage of Gas | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
150 Underground Storage of Gas | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
150 Underground Storage of Gas | D. Total investment cost
150 Underground Storage of Gas | D. Total investment cost
151a Hydrogen Storage - Tanks | A. Cannot be defined since there is no conversion of hydrogen back to electricity in the form of a fuel cell in the system
151a Hydrogen Storage - Tanks | B. The only power input that is considered is the input for the compressor and does not include power needs for the electrolyzer that is making the hydrogen as described in the system definition. Compressor power input decrease of 5% every 10 years
151a Hydrogen Storage - Tanks | C. Calculated in the "Energy Efficiency" section. Compressor efficency lineraly improved by 20% until 2050.
151a Hydrogen Storage - Tanks | D. The charge efficiency is practically the roundrtip efficiency itself as there are almost no losses in the discharge process (See note E)
151a Hydrogen Storage - Tanks | E. Almost no losses during discharge as it is a physical discharge for a pressurized gas from a valve.
151a Hydrogen Storage - Tanks | F. Permeation characteristics are neglibile for Type I tanks, see also Technology-specific data.
151a Hydrogen Storage - Tanks | G. System O&M includes maintenance of the compressor and periodic check of the tanks intergrity.
151a Hydrogen Storage - Tanks | H. System complies with the frequency regulation requirements from Energinet
151a Hydrogen Storage - Tanks | I. No hydrogen storage systems are known to have time of forced outage.
151a Hydrogen Storage - Tanks | J. Compressor consumption is not considered auxiliary. Rest of losses that can be translated into energy losses and consequently more electricity consumption are negligible.
151a Hydrogen Storage - Tanks | K. Losses are below <1%
151a Hydrogen Storage - Tanks | L. Stationary short-medium term storage after production from an electrolyzer
151b Hydrogen Storage - LOHC | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
151b Hydrogen Storage - LOHC | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
151b Hydrogen Storage - LOHC | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
151b Hydrogen Storage - LOHC | D. Total investment cost
151b Hydrogen Storage - LOHC | D. Total investment cost
151b Hydrogen Storage - LOHC | A. Calculated based on techno-economic data of 12tpd plant from Hydrogenious
151b Hydrogen Storage - LOHC | B. Losses during hydrogenation
151b Hydrogen Storage - LOHC | C. Efficiency as received from Hydrogenious
151b Hydrogen Storage - LOHC | D. LOHC uptake does not change with part load operation
151b Hydrogen Storage - LOHC | E. Investment cost on the lines of 5500 tpd scenario.
151b Hydrogen Storage - LOHC | F. Assuming 60% as equipment cost and 40% as installation cost
151b Hydrogen Storage - LOHC | G. Fixed O&M is treated at 4% of CAPEX (Data obtained from hydrogenious)
151b Hydrogen Storage - LOHC | H. Variable O&M is treated as 1% of CAPEX
151b Hydrogen Storage - LOHC | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
151b Hydrogen Storage - LOHC | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
151b Hydrogen Storage - LOHC | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
151c Hydrogen Storage - Caverns | A. Data calculated according to the system defined in the report
151c Hydrogen Storage - Caverns | B. Based on system definition
151c Hydrogen Storage - Caverns | C. Negligible energy losses reported in literature
151c Hydrogen Storage - Caverns | D. One constructed, no outage time is defined
151c Hydrogen Storage - Caverns | E. Pre existing caverns
151c Hydrogen Storage - Caverns | F. Regulation similar to the tanks based on demand supply profile
151c Hydrogen Storage - Caverns | G. O&M cost defined as a percentageof CAPEX in litertaure
151c Hydrogen Storage - Caverns | H. Variable O&M is treated as half of fixed O&M
151c Hydrogen Storage - Caverns | I. Only considering hydrogen pressure, not considering gradient in the cavern (since it depends on the site)
151c Hydrogen Storage - Caverns | J. Negligible permeation losses (Through conversations with Gas energy denmark)
151c Hydrogen Storage - Caverns | J. Negligible permeation losses (Through conversations with Gas energy denmark)
160 Pumped hydro storage | 4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
160 Pumped hydro storage | A. No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
160 Pumped hydro storage | B. Based on the September 2004 exchange rate of 1NOK = 0,12EUR
160 Pumped hydro storage | C. Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
160 Pumped hydro storage | D. Cf. paragraph 'Additional remarks' above.
160 Pumped hydro storage | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
160 Pumped hydro storage | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
160 Pumped hydro storage | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
160 Pumped hydro storage | D. Total investment cost
160 Pumped hydro storage | D. Total investment cost
160 Pumped hydro storage | A. Calculated based on techno-economic data of 12tpd plant from Hydrogenious
160 Pumped hydro storage | B. Losses during hydrogenation
160 Pumped hydro storage | C. Efficiency as received from Hydrogenious
160 Pumped hydro storage | D. LOHC uptake does not change with part load operation
160 Pumped hydro storage | E. Investment cost on the lines of 5500 tpd scenario.
160 Pumped hydro storage | F. Assuming 60% as equipment cost and 40% as installation cost
160 Pumped hydro storage | G. Fixed O&M is treated at 4% of CAPEX (Data obtained from hydrogenious)
160 Pumped hydro storage | H. Variable O&M is treated as 1% of CAPEX
160 Pumped hydro storage | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
160 Pumped hydro storage | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
160 Pumped hydro storage | I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
161 CAES | A. For efficiency it is assumed that that new CAES plants can be constructed with at least the same efficiency as the McIntosh plant.
161 CAES | B. The use of gas in a CAES plant is assumed at the same efficiency as the average use of chemical fuels in the Danish electricity system, i.e. 35% in 2014
161 CAES | C. In general it is assumed that at some point between 2020 and 2030 adiabatic CAES plants will dominate the market. This means that investment costs will increase and performance characteristics will improve.
161 CAES | D. The obtainable ramping rate is likely to decrease after application of thermal energy storage. This is because the heat must be delivered to the storage material, which is a process that cannot be controlled independently.
161 CAES | E. For the costs/kWh in Table 3 the data lying between 0 and 2 EUR/kWh have been disregarded because it is assumed, that only storage costs are included
161 CAES | F. Operation not suitable nor relevant for CAES. Data not available.
161 CAES | G. If a CAES plant is operated as a hot spinning reserve, it can reach the maximum capacity within a few minutes. The emergency startup times from cold conditions at the Huntorf and McIntosh plants are about 5 minutes. Their normal startup times are about 10 to 12 minutes [8]
161 CAES | H. Energy component here taken as the cavern excavating
161 CAES | I. New plants cannot be realized in 2020 because of lead time. Furthermore the upper limit for storage capacity of one unit is determined by cavern volume, which can be obtained practically without.
161 CAES | J. Upper limit in 2050 is based on the author´s assessment of technological development until then.
161 CAES | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
161 CAES | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
161 CAES | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
161 CAES | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
161 CAES | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
162 Flywheels | 4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
162 Flywheels | A. No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
162 Flywheels | B. Based on the September 2004 exchange rate of 1NOK = 0,12EUR
162 Flywheels | C. Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
162 Flywheels | D. Cf. paragraph 'Additional remarks' above.
162 Flywheels | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
162 Flywheels | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
162 Flywheels | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
162 Flywheels | D. Total investment cost
162 Flywheels | D. Total investment cost
162 Flywheels | A. Data informed by WattsUp Power February 2018
162 Flywheels | B. +25 years on mechanics. 15 years on electronics. Informed by WattsUp Power March 2017
162 Flywheels | C. 150 W during upstart procedure for 7 min informed by WattsUp Power. After upstart auxiliary power is included in round trip efficiency
162 Flywheels | D. Informed by WattsUp Power February 2018
162 Flywheels | E. Confer also Table 2
162 Flywheels | F. Please note that the mentioned 1 MW is standard size of one unit that can be assembled to larger entities functioning as “larger units” (somewhat similar to the case of cells in batteries). The displayed financial data is for a 2 MW plant. Flywheels can be connected and provide 20 MW regula...
162 Flywheels | G. Informed by WattsUp Power February 2018
162 Flywheels | H. Loss/day measured by WattsUp Power. The projected losses towards 2050 is justified by results already now obtained by NASA
162 Flywheels | I. The variable costs of flywheels are not directly related to the power put in and out. The data is based on storing (and discharging) 33 MWh/day in 350 days/year. Data from WattsUp Power.
162 Flywheels | J. Displayed price information is based on recent WattsUp Power sales prices for two units (each 1 MW, 100 kWh). Price for one unit of 1 MW and 100 kWh is approx. 0.1 mill EUR. If several units are purchased unit price may be lower than by purchase of two units.
162 Flywheels | K. Based on plans for increasing rotational speed by a factor 3 (WattsUp Power)
162 Flywheels | L. The non-flywheel costs depend on the use of the flywheel. Demanding use patterns may increase non-flywheel costs from the 5 k€ (as included here) to 75 k€/MWh
162 Flywheels | M. Future uncertainties based on author´s best assessment
162 Flywheels | M. Future uncertainties based on author´s best assessment
180 Lithium Ion Battery | A. For efficiency it is assumed that that new CAES plants can be constructed with at least the same efficiency as the McIntosh plant.
180 Lithium Ion Battery | B. The use of gas in a CAES plant is assumed at the same efficiency as the average use of chemical fuels in the Danish electricity system, i.e. 35% in 2014
180 Lithium Ion Battery | C. In general it is assumed that at some point between 2020 and 2030 adiabatic CAES plants will dominate the market. This means that investment costs will increase and performance characteristics will improve.
180 Lithium Ion Battery | D. The obtainable ramping rate is likely to decrease after application of thermal energy storage. This is because the heat must be delivered to the storage material, which is a process that cannot be controlled independently.
180 Lithium Ion Battery | E. For the costs/kWh in Table 3 the data lying between 0 and 2 EUR/kWh have been disregarded because it is assumed, that only storage costs are included
180 Lithium Ion Battery | F. Operation not suitable nor relevant for CAES. Data not available.
180 Lithium Ion Battery | G. If a CAES plant is operated as a hot spinning reserve, it can reach the maximum capacity within a few minutes. The emergency startup times from cold conditions at the Huntorf and McIntosh plants are about 5 minutes. Their normal startup times are about 10 to 12 minutes [8]
180 Lithium Ion Battery | H. Energy component here taken as the cavern excavating
180 Lithium Ion Battery | I. New plants cannot be realized in 2020 because of lead time. Furthermore the upper limit for storage capacity of one unit is determined by cavern volume, which can be obtained practically without.
180 Lithium Ion Battery | J. Upper limit in 2050 is based on the author´s assessment of technological development until then.
180 Lithium Ion Battery | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
180 Lithium Ion Battery | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
180 Lithium Ion Battery | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
180 Lithium Ion Battery | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
180 Lithium Ion Battery | K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
181 Vanadium Redox Flow Battery | 4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
181 Vanadium Redox Flow Battery | A. No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
181 Vanadium Redox Flow Battery | B. Based on the September 2004 exchange rate of 1NOK = 0,12EUR
181 Vanadium Redox Flow Battery | C. Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
181 Vanadium Redox Flow Battery | D. Cf. paragraph 'Additional remarks' above.
181 Vanadium Redox Flow Battery | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
181 Vanadium Redox Flow Battery | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
181 Vanadium Redox Flow Battery | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
181 Vanadium Redox Flow Battery | D. Total investment cost
181 Vanadium Redox Flow Battery | D. Total investment cost
181 Vanadium Redox Flow Battery | A. Data informed by WattsUp Power February 2018
181 Vanadium Redox Flow Battery | B. +25 years on mechanics. 15 years on electronics. Informed by WattsUp Power March 2017
181 Vanadium Redox Flow Battery | C. 150 W during upstart procedure for 7 min informed by WattsUp Power. After upstart auxiliary power is included in round trip efficiency
181 Vanadium Redox Flow Battery | D. Informed by WattsUp Power February 2018
181 Vanadium Redox Flow Battery | E. Confer also Table 2
181 Vanadium Redox Flow Battery | A. One Uni.System unit from UniEnergy Technologies. Installation sizes vary from tens of kW to hundreds of MW.
181 Vanadium Redox Flow Battery | B. Efficiency varies depending on use.
181 Vanadium Redox Flow Battery | C. Energy losses depend on idle situation. If pumps are off and electrolyte not present in the reaction stack no energy loss occurs. This increases response time (see above). Self-discharge only occurs for electrolyte inside the reaction stack. This is a relatively small volume and the self-disch...
181 Vanadium Redox Flow Battery | D. Some companies guarantee at least 99.5% uptime.
181 Vanadium Redox Flow Battery | E. Depends highly on the installation.
181 Vanadium Redox Flow Battery | Time is less than 100 ms for idle situation with electrolyte in reaction stack and pumps on [4]. Less the 1 s if electrolyte must first be pumped [5]. Less than 1 min if pumps are not on [5]. PCS might be limiting the response time.
181 Vanadium Redox Flow Battery | G. Might in practice be limited by PCS.
181 Vanadium Redox Flow Battery | H. Valid for installations with rated discharge times of 4 hours. Use equation in “Prediction of performance and cost” above to calculate for installations with a different rated discharge time.
181 Vanadium Redox Flow Battery | I. Composed of both electrolyte etc. at 347 EUR/kWh and stack at 1313 EUR/kW [22].
181 Vanadium Redox Flow Battery | J. Value for utility T&D installations with discharge time of 4 hours used.
181 Vanadium Redox Flow Battery | K. Manufactures state unlimited number of cycles during technical lifetime [4], [5].
181 Vanadium Redox Flow Battery | L. Varies with capacity to storage ratio. Is significantly lower for some manufactures.
181 Vanadium Redox Flow Battery | M. Uncertainties are based on a qualified guess.
181 Vanadium Redox Flow Battery | M. Uncertainties are based on a qualified guess.
181 Vanadium Redox Flow Battery | M. Uncertainties are based on a qualified guess.
181 Vanadium Redox Flow Battery | M. Uncertainties are based on a qualified guess.
181 Vanadium Redox Flow Battery | M. Uncertainties are based on a qualified guess.
181 Vanadium Redox Flow Battery | [1] M. Manahan, N. Jewell, D. Link, and B. Westlake, “Program on Technology Innovation: Assessment of Flow Battery Technologies for Stationary Applications,” EPRI, 2016.
181 Vanadium Redox Flow Battery | [2] M. Guarnieri, P. Mattavelli, G. Petrone, and G. Spagnuolo, “Vanadium Redox Flow Batteries: Potentials and Challenges of an Emerging Storage Technology,” IEEE Ind. Electron. Mag., vol. 10, no. 4, pp. 20–31, 2016.
181 Vanadium Redox Flow Battery | [3] M. Skyllas-Kazacos, “SECONDARY BATTERIES – FLOW SYSTEMS ¦ Vanadium Redox-Flow Batteries,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 444–453.
181 Vanadium Redox Flow Battery | [4] UniEnergy Technologies, “Uni.System product data,” 2016.
181 Vanadium Redox Flow Battery | [5] Vionx Energy, “VNX 1000 SERIES Product data,” 2017.
181 Vanadium Redox Flow Battery | [6] UniEnergy Technologies, Product material: Maximizing Value Thorugh UET Energy Storage. 2015.
181 Vanadium Redox Flow Battery | [7] Z. Yang et al., “Electrochemical Energy Storage for Green Grid,” Chem. Rev., vol. 111, no. 5, pp. 3577–3613, May 2011.
181 Vanadium Redox Flow Battery | [8] Sumitomo Electric Group, REDOX FLOW BATTERY: Product material. 2016.
181 Vanadium Redox Flow Battery | [9] “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
181 Vanadium Redox Flow Battery | [10] Sumitomo Electric Group, “Container Type Redox Flow Battery System,” 2017.
181 Vanadium Redox Flow Battery | [11] IEC, “Electrical Energy Storage,” 2011.
181 Vanadium Redox Flow Battery | [12] “Sumitomo Electric Industries, Ltd. ¦ Press Release (2013) Selected to be Subsidized by the Governmental Program for Urgent Demonstration Project of Large-scale Energy Storage Systems.” [Online]. Available: http://global-sei.com/news/press/13/prs088_s.html. [Accessed: 30-Mar-2017].
181 Vanadium Redox Flow Battery | [13] J. Cho, S. Jeong, and Y. Kim, “Commercial and research battery technologies for electrical energy storage applications,” Prog. Energy Combust. Sci., vol. 48, pp. 84–101, Jun. 2015.
181 Vanadium Redox Flow Battery | [14] T. Biesheuvel and M. Burton, “It’s Boom Time for Vanadium, Ruthenium and Cobalt - Bloomberg,” Bloomberg Markets, 2017. [Online]. Available: https://www.bloomberg.com/news/articles/2017-08-23/obscure-metal-used-to-fight-crusaders-has-surged-67-in-a-month. [Accessed: 06-Dec-2017].
181 Vanadium Redox Flow Battery | [15] C. K. Charlotte Radford, Anna Xu, “GLOBAL VANADIUM WRAP: Prices rise across the board amid tight supply of V2O5 ¦ Metal Bulletin.com,” 2017. [Online]. Available: https://www.metalbulletin.com/Article/3768052/GLOBAL-VANADIUM-WRAP-Prices-rise-across-the-board-amid-tight-supply-of-V2O5.html. [A...
181 Vanadium Redox Flow Battery | [16] M. Moore, R. Counce, J. Watson, and T. Zawodzinski, “A Comparison of the Capital Costs of a Vanadium Redox-Flow Battery and a Regenerative Hydrogen-Vanadium Fuel Cell,” J. Adv. Chem. Eng., vol. 5, no. 4, pp. 5–7, 2015.
181 Vanadium Redox Flow Battery | [17] M. C. S. U.S. Geological Survey, “VANADIUM (Data in metric tons of vanadium content unless otherwise noted),” 2014.
181 Vanadium Redox Flow Battery | [18] O. Schmidt, A. Hawkes, A. Gambhir, and I. Staffell, “The future cost of electrical energy storage based on experience rates,” Nat. Energy, vol. 2, no. 8, p. 17110, Jul. 2017.
181 Vanadium Redox Flow Battery | [19] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
181 Vanadium Redox Flow Battery | [20] L. Baumann and E. Boggasch, “Experimental assessment of hydrogen systems and vanadium-redox-flow-batteries for increasing the self-consumption of photovoltaic energy in buildings,” Int. J. Hydrogen Energy, vol. 41, no. 2, pp. 740–751, 2016.
181 Vanadium Redox Flow Battery | [21] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
181 Vanadium Redox Flow Battery | [22] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
181 Vanadium Redox Flow Battery | [23] G. Kear, A. A. Shah, and F. C. Walsh, “Development of the all-vanadium redox flow battery for energy storage: a review of technological, financial and policy aspects,” Int. J. Energy Res., vol. 36, no. 11, pp. 1105–1120, Sep. 2012.
181 Vanadium Redox Flow Battery | [24] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
181 Vanadium Redox Flow Battery | [25] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
181 Vanadium Redox Flow Battery | [26] M. Skyllas-Kazacos and J. F. McCann, “Chapter 10 – Vanadium redox flow batteries (VRBs) for medium- and large-scale energy storage,” in Advances in Batteries for Medium and Large-Scale Energy Storage, 2015, pp. 329–386.
181 Vanadium Redox Flow Battery | [27] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
181 Vanadium Redox Flow Battery | [28] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
181 Vanadium Redox Flow Battery | [29] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
181 Vanadium Redox Flow Battery | [30] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
181 Vanadium Redox Flow Battery | [31] I. Renewable Energy Agency, “IRENA-IEA-ETSAP Technology Brief 5: Electricity Storage,” 2012.
182 Na-S Battery | A. For efficiency it is assumed that that new CAES plants can be constructed with at least the same efficiency as the McIntosh plant.
182 Na-S Battery | B. The use of gas in a CAES plant is assumed at the same efficiency as the average use of chemical fuels in the Danish electricity system, i.e. 35% in 2014
182 Na-S Battery | C. In general it is assumed that at some point between 2020 and 2030 adiabatic CAES plants will dominate the market. This means that investment costs will increase and performance characteristics will improve.
182 Na-S Battery | A. Specific Italian installation from 2015 used here as example. Assuming installations similar to Buzen City discussed above to become standard in the future.
182 Na-S Battery | B. Highly modular technology type with near linear scaling between total cost and installation size. Power and storage capacity cannot be varied independently.
182 Na-S Battery | C. Grid size unit including balancing and auxiliary losses. Excluding converters. Assumes no improvement between 2030 and 2050.
182 Na-S Battery | D. Ohmic losses maintain the temperature of the battery during operation. Losses are thus included in round trip efficiency [7]. No electrical self-discharge. If idle the heat loss is as much as 1 % of storage capacity/hour but highly variational. IRENA reports as “worst” value og 1.0 % [26]
182 Na-S Battery | E. Forced outage is minimal. Only reported case is a 2011 fire incident [9].
182 Na-S Battery | F. On the order of 1 h/year.
182 Na-S Battery | G. Assumptions for development and uncertainty discussed above in “Prediction of performance” and “Uncertainty”.
182 Na-S Battery | H. Due to absence of predictions in literature, no development is assumed as an estimate.
182 Na-S Battery | I. Measurement. Possibly limited by PCS.
182 Na-S Battery | J. Includes “Batteries” from reference [22] for 2015 values.
182 Na-S Battery | K. Includes “PCS-SCI”, “Auxiliary equipment”, and “Switching and actuating equipment” from reference [22] for 2015 values.
182 Na-S Battery | L. Highly uncertain. Reported in range 2000 to 17300 EUR2015/MW/year [24]
182 Na-S Battery | M. Does not include replacement costs. The batteries do not need replacement within lifetime [13],[10].
182 Na-S Battery | N. See Figure 5.
182 Na-S Battery | O. Data for standard NGK container unit.
182 Na-S Battery | P. Not the technological maximum values, i.e., the density of single cells, but the specifications for a full market-standard commercial product.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
182 Na-S Battery | Q. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | 4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
183 Na-NiCl2 Battery | A. No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
183 Na-NiCl2 Battery | B. Based on the September 2004 exchange rate of 1NOK = 0,12EUR
183 Na-NiCl2 Battery | C. Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
183 Na-NiCl2 Battery | D. Cf. paragraph 'Additional remarks' above.
183 Na-NiCl2 Battery | A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
183 Na-NiCl2 Battery | B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
183 Na-NiCl2 Battery | C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
183 Na-NiCl2 Battery | D. Total investment cost
183 Na-NiCl2 Battery | D. Total investment cost
183 Na-NiCl2 Battery | A. Data informed by WattsUp Power February 2018
183 Na-NiCl2 Battery | B. +25 years on mechanics. 15 years on electronics. Informed by WattsUp Power March 2017
183 Na-NiCl2 Battery | C. 150 W during upstart procedure for 7 min informed by WattsUp Power. After upstart auxiliary power is included in round trip efficiency
183 Na-NiCl2 Battery | D. Informed by WattsUp Power February 2018
183 Na-NiCl2 Battery | E. Confer also Table 2
183 Na-NiCl2 Battery | A. One Uni.System unit from UniEnergy Technologies. Installation sizes vary from tens of kW to hundreds of MW.
183 Na-NiCl2 Battery | B. Efficiency varies depending on use.
183 Na-NiCl2 Battery | C. Energy losses depend on idle situation. If pumps are off and electrolyte not present in the reaction stack no energy loss occurs. This increases response time (see above). Self-discharge only occurs for electrolyte inside the reaction stack. This is a relatively small volume and the self-disch...
183 Na-NiCl2 Battery | D. Some companies guarantee at least 99.5% uptime.
183 Na-NiCl2 Battery | E. Depends highly on the installation.
183 Na-NiCl2 Battery | Time is less than 100 ms for idle situation with electrolyte in reaction stack and pumps on [4]. Less the 1 s if electrolyte must first be pumped [5]. Less than 1 min if pumps are not on [5]. PCS might be limiting the response time.
183 Na-NiCl2 Battery | G. Might in practice be limited by PCS.
183 Na-NiCl2 Battery | H. Valid for installations with rated discharge times of 4 hours. Use equation in “Prediction of performance and cost” above to calculate for installations with a different rated discharge time.
183 Na-NiCl2 Battery | I. Composed of both electrolyte etc. at 347 EUR/kWh and stack at 1313 EUR/kW [22].
183 Na-NiCl2 Battery | J. Value for utility T&D installations with discharge time of 4 hours used.
183 Na-NiCl2 Battery | K. Manufactures state unlimited number of cycles during technical lifetime [4], [5].
183 Na-NiCl2 Battery | L. Varies with capacity to storage ratio. Is significantly lower for some manufactures.
183 Na-NiCl2 Battery | M. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | M. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | M. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | M. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | M. Uncertainties are based on a qualified guess.
183 Na-NiCl2 Battery | [1] M. Manahan, N. Jewell, D. Link, and B. Westlake, “Program on Technology Innovation: Assessment of Flow Battery Technologies for Stationary Applications,” EPRI, 2016.
183 Na-NiCl2 Battery | [2] M. Guarnieri, P. Mattavelli, G. Petrone, and G. Spagnuolo, “Vanadium Redox Flow Batteries: Potentials and Challenges of an Emerging Storage Technology,” IEEE Ind. Electron. Mag., vol. 10, no. 4, pp. 20–31, 2016.
183 Na-NiCl2 Battery | [3] M. Skyllas-Kazacos, “SECONDARY BATTERIES – FLOW SYSTEMS ¦ Vanadium Redox-Flow Batteries,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 444–453.
183 Na-NiCl2 Battery | [4] UniEnergy Technologies, “Uni.System product data,” 2016.
183 Na-NiCl2 Battery | [5] Vionx Energy, “VNX 1000 SERIES Product data,” 2017.
183 Na-NiCl2 Battery | [6] UniEnergy Technologies, Product material: Maximizing Value Thorugh UET Energy Storage. 2015.
183 Na-NiCl2 Battery | [7] Z. Yang et al., “Electrochemical Energy Storage for Green Grid,” Chem. Rev., vol. 111, no. 5, pp. 3577–3613, May 2011.
183 Na-NiCl2 Battery | [8] Sumitomo Electric Group, REDOX FLOW BATTERY: Product material. 2016.
183 Na-NiCl2 Battery | [9] “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
183 Na-NiCl2 Battery | [10] Sumitomo Electric Group, “Container Type Redox Flow Battery System,” 2017.
183 Na-NiCl2 Battery | [11] IEC, “Electrical Energy Storage,” 2011.
183 Na-NiCl2 Battery | [12] “Sumitomo Electric Industries, Ltd. ¦ Press Release (2013) Selected to be Subsidized by the Governmental Program for Urgent Demonstration Project of Large-scale Energy Storage Systems.” [Online]. Available: http://global-sei.com/news/press/13/prs088_s.html. [Accessed: 30-Mar-2017].
183 Na-NiCl2 Battery | [13] J. Cho, S. Jeong, and Y. Kim, “Commercial and research battery technologies for electrical energy storage applications,” Prog. Energy Combust. Sci., vol. 48, pp. 84–101, Jun. 2015.
183 Na-NiCl2 Battery | [14] T. Biesheuvel and M. Burton, “It’s Boom Time for Vanadium, Ruthenium and Cobalt - Bloomberg,” Bloomberg Markets, 2017. [Online]. Available: https://www.bloomberg.com/news/articles/2017-08-23/obscure-metal-used-to-fight-crusaders-has-surged-67-in-a-month. [Accessed: 06-Dec-2017].
183 Na-NiCl2 Battery | [15] C. K. Charlotte Radford, Anna Xu, “GLOBAL VANADIUM WRAP: Prices rise across the board amid tight supply of V2O5 ¦ Metal Bulletin.com,” 2017. [Online]. Available: https://www.metalbulletin.com/Article/3768052/GLOBAL-VANADIUM-WRAP-Prices-rise-across-the-board-amid-tight-supply-of-V2O5.html. [A...
183 Na-NiCl2 Battery | [16] M. Moore, R. Counce, J. Watson, and T. Zawodzinski, “A Comparison of the Capital Costs of a Vanadium Redox-Flow Battery and a Regenerative Hydrogen-Vanadium Fuel Cell,” J. Adv. Chem. Eng., vol. 5, no. 4, pp. 5–7, 2015.
183 Na-NiCl2 Battery | [17] M. C. S. U.S. Geological Survey, “VANADIUM (Data in metric tons of vanadium content unless otherwise noted),” 2014.
183 Na-NiCl2 Battery | [18] O. Schmidt, A. Hawkes, A. Gambhir, and I. Staffell, “The future cost of electrical energy storage based on experience rates,” Nat. Energy, vol. 2, no. 8, p. 17110, Jul. 2017.
183 Na-NiCl2 Battery | [19] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
183 Na-NiCl2 Battery | [20] L. Baumann and E. Boggasch, “Experimental assessment of hydrogen systems and vanadium-redox-flow-batteries for increasing the self-consumption of photovoltaic energy in buildings,” Int. J. Hydrogen Energy, vol. 41, no. 2, pp. 740–751, 2016.
183 Na-NiCl2 Battery | [21] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
183 Na-NiCl2 Battery | [22] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
183 Na-NiCl2 Battery | [23] G. Kear, A. A. Shah, and F. C. Walsh, “Development of the all-vanadium redox flow battery for energy storage: a review of technological, financial and policy aspects,” Int. J. Energy Res., vol. 36, no. 11, pp. 1105–1120, Sep. 2012.
183 Na-NiCl2 Battery | [24] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
183 Na-NiCl2 Battery | [25] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
183 Na-NiCl2 Battery | [26] M. Skyllas-Kazacos and J. F. McCann, “Chapter 10 – Vanadium redox flow batteries (VRBs) for medium- and large-scale energy storage,” in Advances in Batteries for Medium and Large-Scale Energy Storage, 2015, pp. 329–386.
183 Na-NiCl2 Battery | [27] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
183 Na-NiCl2 Battery | [28] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
183 Na-NiCl2 Battery | [29] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
183 Na-NiCl2 Battery | [30] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
183 Na-NiCl2 Battery | [31] I. Renewable Energy Agency, “IRENA-IEA-ETSAP Technology Brief 5: Electricity Storage,” 2012.

## Ref
ws | description
140 PTES seasonal | 1. PlanEnergi, Teknologisk Institut, GEO & Grøn Energi, 2013, Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer
140 PTES seasonal | 5. PlanEnergi 2017, based on latest three projects and tender material for two planned PTES [2017/18)
140 PTES seasonal | 12. Danish Energy Agency, 1988, Energy Technology Catalogue 38.01
140 PTES seasonal | 14. Schmidt, Sørensen [2018). Monitoring Results from Large Scale Heat storages for District Heating in Denmark. 14th International Conference on Energy Storage, 25-28 April 2018, Adana, Turkey
142 Small scale hot water tank | 5. Metro-Therm A/S, 2019, sales department and homepage.
142 Small scale hot water tank | 6. PlanEnergi, 2019
142 Small scale hot water tank | 8. Danish standard, "Specification for indirectly heated unvented (closed) storage water heaters", DS12897:2016
160 Pumped hydro storage | 1. BKK, presentation on Nygard Pumpekraftverk
160 Pumped hydro storage | 2. Tonstad Pumpekraftverk, Sira-Kvina kraftselskap, 2002
160 Pumped hydro storage | 3. BKK and Sira-Kvina (1-2% of investment)
160 Pumped hydro storage | 4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
161 CAES | 1. S. Karellas and N. Tzouganatos, "Comparison of the performance of compressed-air and hydrogen," vol. 29, 2014.
161 CAES | 2. E. Barbour, "http://energystoragesense.com/compressed-air-energy-storage/," [Online].
161 CAES | 3. S. Zunft, S. Freund and E. M. Schlichtenmayer, "Large Scale Electricity Storage with Adiabatic CAES," Paris, November 2014.
161 CAES | 4. "Geological storage in Northern Ireland," Geological Survay of Northern Ireland. [Online].
161 CAES | 5. P. Johnson, "ASSESSMENT OF COMPRESSED AIR ENERGY STORAGE SYSTEM (CAES)," Thesis Submitted to the University of Tennessee, University of Tennessee at Chattanooga, Chattanooga, Tenessee, USA, 2014.
161 CAES | 6. R. W. S. Succar, "Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power," Energy Systems Analysis Group, Princeton Environmental Institute, Princeton University, April 2008.
161 CAES | 7. J. W. X. Luo, "Overview on current development on Compressed Air Energy Storage, EERA Technical Report – CAES.," School of engineering, University of Warwick. Available on http://integratedenergystorage.org/. Accessed February 2017, December 2013.
161 CAES | 8. I. Gyuk and S. Eckroad, "EPRI-DOE Hanbook of Energy Storage for Transmission and Distribution Applications,1001834, Final Report," EPRI and DOE, December 2003.
161 CAES | 9. Nakhamkin and Brotel, "Second generation compressed air storage," in Energy Storage Forum Europe, Rome, 2012.
161 CAES | 10. F. Crotogino, K.-U. Mohmeyer and R. Scharf, "Huntorf CAES/More than 20 yeasr of successful operation," Orlando, April 2001.
161 CAES | 11. "https://dddusmma.wordpress.com/2014/05/30/storage-is-essential-for-wind-and-solar/," Department of Energy, USA. [Online]. [Accessed 2017].
161 CAES | 12. "https://dddusmma.wordpress.com/2015/03/17/the-quest-for-storing-electricity/," 17 March 2015. [Online]. [Accessed 2017].
161 CAES | 13. A. Wänn, P. Leahy, M. Reidy, S. Doyle, H. Dalton and P. Barr, "Environmental performance of existing energy storage installations. Deliverable D.3.1. Available on www.store-project.eu. Accessed February 2017," stoRE project, 2012.
161 CAES | 14. E. Bouman, M. M. Øberg and E. G. Hertwich, "LIFE CYCLE ASSESSMENT OF COMPRESSED AIR ENERGY STORAGE (CAES)," Gothenburg, 2013.
161 CAES | 15. "ADELE – ADIABATIC COMPRESSED-AIR ENERGY STORAGE FOR ELECTRICITY SUPPLY. RWE Brochure.," RWE Power AG, Cologne, 2010.
161 CAES | 16. "Energy Storage Technology Roadmap, Technology Annex, p. 5," International Energy Agency, March 2014.
161 CAES | 17. Gaelectric. Accesses February 2017. [Online].
161 CAES | 18. "Gaelectric energy storage: The missing link. Brochure by Gaelectric. Availble on http://www.gaelectric.ie/energy-storage-publications/. Accessed February 2017," Gaelectric.
161 CAES | 19. [Online].
161 CAES | 20. D.Rastler, A. Akhil and D. Gauntlett, "Energy Storage System Costs 2011 update. Excecutive summary.," 2011.
161 CAES | 21. "InflationData.com," InflationData, 2017. [Online]. [Accessed March 2017].
161 CAES | 22. E. Drury, P. Denholm and R. Sioshansi, "The Value of Compressed Air Energy Storage in Energy and Reserve Markets," National Renewable Energy Laboratory, USA, 2009.
161 CAES | 23. "Handbook for Energy Storage for Transmission or Distribution Applications. Report No. 1007189. Technical Update December 2002. Document can be found at: www.epri.com," EPRI, 2002.
161 CAES | 24. "COST AND PERFORMANCE DATA FOR POWER GENERATION TECHNOLOGIES, Report prepared for the National Renewable Energy Laboratory, Avaliable on https://www.bv.com/docs/reports-studies/nrel-cost-report.pdf (Accessed February 2017)," Black & Veatch, 2012.
161 CAES | 25. B. McGrail, "Techno-economic Performance Evaluation of Compressed Air Energy Storage in the Pacific Northwest. Available on http://caes.pnnl.gov/pdf/PNNL-22235.pdf. Accessed February 2017," Pacific Northwes National Laboratory (operated by Batelle), 2013.
161 CAES | 26. "Materials Roadmap Enabling Low Carbon Energy Technologies, Commission Staff Working Paper," European Commission, Brussels, 2011.
161 CAES | 27. A. Bary, "Storing natural gas underground. Available on https://www.slb.com/~/media/Files/resources/oilfield_review/ors02/sum02/p2_17.pdf (Accessed February 2017)," Oilfield review, 2002.
161 CAES | 28. A. Cavallo, "Controllable and affordable utility-scale electricity from intermittent wind resources and compressed air energy storage (CAES)," vol. 32, pp. 120-127, 2007.
161 CAES | 29. J. T. Dasand, "Compressed Air Energy Storage (Educational Chapter)," Iowa state University, 2012.
161 CAES | 30. E. M. G.Locatellia, "Assessing the economics of large Energy Storage Plants with an optimisation methodology," vol. 83, April 2015.
161 CAES | 31. "Energy Storage News," Energy Storage News, 2016. [Online].
161 CAES | 32. P. Tayler, "Pathways for Energy Storage in the UK, Report 007," The Centre for Low Carbon Futures, March 2012.
161 CAES | 33. H. Lund and G. Salgi, "The role of compressed air energy storage (CAES) in future sustainable energy systems," vol. 50, pp. 1172-1179, 2009.
161 CAES | 34. M. Nakhamkin, M. Chiruvolu and C. Daniel, "Available Compressed Air Energy Storage (CAES) Plant Concepts. Available on http://www.espcinc.com/library/PowerGen_2007_paper.pdf. Accessed February 2017," ESPC and Towngas International Company, 2007.
161 CAES | 35. J. Simmons, "Study of Compressed Air Energy Storage with Grid and Photovoltaic Energy Generation," The Arizona Research Institute for Solar Energy (AzRISE) - APS Final Draft Report., University of Arizona, 2010.
162 Flywheels | [1] "http://www.elp.com/articles/2016/01/amber-kinetics-signs-flywheel-energy-storage-contract-with-pg-e.html," 2016. [Online]. [Accessed March 2017].
162 Flywheels | [2] e. a. I. Gyuk, "Grid Energy Storage," US Department of Energy, 2013.
162 Flywheels | [3] S.-i. Inage, "Prospects of Electricity Storage in Decarbonised Power Grids, IEA Working Paper Series," OECD/IEA, 2009.
162 Flywheels | [4] "Toshiba Leading Innovation," Toshiba. [Online]. [Accessed March 2017].
162 Flywheels | [5] "Fact sheet. Frequency Regulation and Flywheels," Beacon Power, 2010. Archived March 2017. Available on https://web.archive.org/web/20100331042630/http://www.beaconpower.com/files/Flywheel_FR-Fact-Sheet.pdf.
162 Flywheels | [6] "http://beaconpower.com," Beacon Power. [Online]. [Accessed March 2017].
162 Flywheels | [7] B. Z. a. S. Syri, "Electrical Energy Storage Systems: A comparative life cycle cost analysis," Renewable and Sustainable Energy Reviews, vol. 42, pp. 569-596, 2015.
162 Flywheels | [8] I. P. ,. E. S. Gyuk, "EPRI-DOE Handbook of Energy Storage for Transmission & Distribution Applications 1001834," US Department of Energy, Washington, 2003.
162 Flywheels | [9] "timesunion," Times Union, 2011. [Online]. [Accessed March 2017].
162 Flywheels | [10] "Joint EASE/EERA recommendations for a European Energy Storage Technology Development Roadmap towards 2030," EASE and EERA, Brussels, 2013.
162 Flywheels | [11] "Technology Roadmap, Energy Storage," International Energy Agency, Paris, 2013.
162 Flywheels | [12] N. K. Kohli, "Short-Term backup power through flywheel energy storage system. Available on https://www.slideshare.net/Drnavinkumarkohli/ppt-fly-wheel-navin-kohli (Accessed March 2017)," 2012.
162 Flywheels | [13] S. o. A. E. I. SAE, "https://global.ihs.com/doc_detail.cfm?rid=GS&&item_s_key=00138611," IHS Markit, 2013. [Online]. [Accessed March 2017].
162 Flywheels | [14] "Electrical Energy Storage," International Electrotechnical Commission, Geneva, Switzerland, 2011.
162 Flywheels | [15] 2. Private communication with WattsUp Power.
162 Flywheels | [16] W. Torell, "Lifecycle C arbon Footprint Analysis of Batteries vs. Flywheels, White Paper 209," Schneider Electric, 2015.
162 Flywheels | [17] W. V. H. Susan M. Schoenung, "Long- vs. Short-Term Energy Storage Technologies Analysis. A Life-Cycle Cost Study," Sandia National Laboratories, Albuquerque, New Mexico 87185 and Livermore, California 94550, 2003.
162 Flywheels | [18] "Lazard´s levelized cost of storage - Version 2.0," Lazard, 2016.
162 Flywheels | [19] e. a. P. Tayler, "Pathways for Energy Storage in the UK, Report 007," The Centre for Low Carbon Futures, March 2012.
162 Flywheels | [20] "https://www.calnetix.com/resource/flywheels/advantages-flywheels," Calnetix. [Online]. [Accessed March 2017].
162 Flywheels | [21] "http://www.climatetechwiki.org/technology/jiqweb-es-fw," [Online].
162 Flywheels | [22] P. N. N. L. Daryl Brown, "Federal Technology Alert. DOE/EE-0286," Federal Energy Management Program, 2003.
162 Flywheels | [23] "InflationData.com," InflationData, 2017. [Online]. [Accessed 2017].
162 Flywheels | [24] "Materials Roadmap Enabling Low Carbon Energy Technologies, Commission Staff Working Paper," European Commission, Brussels, 2011.
162 Flywheels | [25] "energy.gov," 2010. [Online]. [Accessed March 2017].
162 Flywheels | [26] "Scientific American," Scientific American, 2011. [Online]. [Accessed March 2017].
162 Flywheels | [27] e. a. M. Hedlund, "Flywheel Energy Storage for Automotive Applications," Energies, vol. 8, pp. 10636-10663, 2015.
162 Flywheels | [28] 2009. [Online]. [Accessed March 2017].
162 Flywheels | [29] Memoori, Smart Building Resesearch, 2017. [Online]. [Accessed MArch 2017].
182 Na-S Battery | [1] NGK Insulators LTD, “Case Studies.” pp. 1–13, 2016.
182 Na-S Battery | [2] “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
182 Na-S Battery | [3] IEC, “Electrical Energy Storage,” 2011.
182 Na-S Battery | [4] C.-H. Dustmann and A. Bito, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS ¦ Safety,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 324–333.
182 Na-S Battery | [5] B. Dunn, H. Kamath, and J.-M. Tarascon, “Electrical Energy Storage for the Grid: A Battery of Choices,” Science (80-. )., vol. 334, no. 6058, pp. 928–935, 2011.
182 Na-S Battery | [6] J. Cho, S. Jeong, and Y. Kim, “Commercial and research battery technologies for electrical energy storage applications,” Prog. Energy Combust. Sci., vol. 48, pp. 84–101, Jun. 2015.
182 Na-S Battery | [7] J. Garche and C. K. Dyer, Encyclopedia of electrochemical power sources. Academic Press, 2009.
182 Na-S Battery | [8] R. Holze, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS: Sodium-Sulfur,” in Encyclopedia of Electrochemical Power Systems, vol. 200, 2009, pp. 302–311.
182 Na-S Battery | [9] M. Andriollo et al., “Energy intensive electrochemical storage in Italy: 34.8 MW sodium-sulphur secondary cells,” J. Energy Storage, vol. 5, pp. 146–155, Feb. 2016.
182 Na-S Battery | [10] NGK Insulators LTD, “Structure of NAS Energy Storage System,” 2016. [Online]. Available: https://www.ngk.co.jp/nas/specs/.
182 Na-S Battery | [11] H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
182 Na-S Battery | [12] NGK Insulators LTD, “The World’s Largest NAS Battery Installation Commences Operation Short Installation Period Achieved through Containerized, Compact Format,” 2016. [Online]. Available: http://www.ngk.co.jp/english/news/2016/0303.html.
182 Na-S Battery | [13] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
182 Na-S Battery | [14] NGK Insulators LTD, “Comparison of Battery Technologies ¦ Why NAS? ¦ NAS.” [Online]. Available: https://www.ngk.co.jp/nas/why/comparison.html. [Accessed: 13-Sep-2017].
182 Na-S Battery | [15] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
182 Na-S Battery | [16] Z. Wen, Y. Hu, X. Wu, J. Han, and Z. Gu, “Main Challenges for High Performance NAS Battery: Materials and Interfaces,” Adv. Funct. Mater., vol. 23, no. 8, pp. 1005–1018, Feb. 2013.
182 Na-S Battery | [17] G. Kim, Y.-C. Park, Y. Lee, N. Cho, C.-S. Kim, and K. Jung, “The effect of cathode felt geometries on electrochemical characteristics of sodium sulfur (NaS) cells: Planar vs. tubular,” J. Power Sources, vol. 325, pp. 238–245, Sep. 2016.
182 Na-S Battery | [18] S. I. Kim, W. Il Park, K. Jung, and C.-S. Kim, “An innovative electronically-conducting matrix of the cathode for sodium sulfur battery,” J. Power Sources, vol. 320, pp. 37–42, Jul. 2016.
182 Na-S Battery | [19] K. . Ahlbrecht, C. Bucharsky, M. Holzapfel, J. Tübke, and M. J. Hoffmann, “Investigation of the wetting behavior of Na and Na alloys on uncoated and coated Na-β”-alumina at temperatures below 150 °C,” Ionics (Kiel)., pp. 1–9, Mar. 2017.
182 Na-S Battery | [20] X. Yu and A. Manthiram, “Ambient-Temperature Sodium-Sulfur Batteries with a Sodiated Nafion Membrane and a Carbon Nanofiber-Activated Carbon Composite Electrode,” Adv. Energy Mater., vol. 5, no. 12, pp. 1–6, 2015.
182 Na-S Battery | [21] X. Yu and A. Manthiram, “Performance Enhancement and Mechanistic Studies of Room-Temperature Sodium–Sulfur Batteries with a Carbon-Coated Functional Nafion Separator and a Na 2 S/Activated Carbon Nanofiber Cathode,” Chem. Mater., vol. 28, no. 3, pp. 896–905, Feb. 2016.
182 Na-S Battery | [22] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
182 Na-S Battery | [23] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
182 Na-S Battery | [24] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
182 Na-S Battery | [25] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
182 Na-S Battery | [26] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
182 Na-S Battery | [27] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
182 Na-S Battery | [28] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
182 Na-S Battery | [29] R. Benato et al., “Sodium nickel chloride battery technology for large-scale stationary storage in the high voltage network,” J. Power Sources, vol. 293, pp. 127–136, 2015.
182 Na-S Battery | [30] G. L. Soloveichik, “Battery Technologies for Large-Scale Stationary Energy Storage,” Annu. Rev. Chem. Biomol. Eng, vol. 2, pp. 503–27, 2011.

## 140 PTES seasonal
Technology |  | Pit Thermal Energy Storage [PTES]
year |  | 2020 | 2025 | 2030 | 2035 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat
| Application | System | System | System | System | System | System | System | System | System | System
| Energy storage capacity for one unit [MWh] | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
| Output capacity for one unit [MW] | 30 | 30 | 150 | 200 | 200 | 200 | 30 | 150 | 30 | 200 | A | 5
| Input capacity for one unit [MW] | 30 | 30 | 150 | 200 | 200 | 200 | 30 | 150 | 30 | 200 | A | 5
| Round trip efficiency [%] | 80% | 80% | 80% | 80% | 80% | 80% | 75% | 90% | 80% | 95% | B, I | 1, 5, 14, 23
| - Charge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | B
| - Discharge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | B
| Energy losses during storage [K/day] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.04 | 0.1 | 0.04 | 0.1 | B | 12
| Auxiliary electricity consumption [% of output] | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | C | 5
Forced outage [%] | bar: ctrl to Upper
Planned outage [weeks/year] | bar: ctrl to Upper
| Technical lifetime [years] | 20 | 30 | 30 | 30 | 30 | 30 | 20 | 40 | 30 | 50 | D | 24
| Construction time [years] | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | E
Regulation ability
Primary regulation [%/30 sec]
Secondary regulation [%/minute]
Financial data
| Specific investment [M€/GWh Capacity] | 1.0622 | 1.0622 | 1.0622 | 1.0622 | 0.98256 | 0.90289 | 0.90289 | 1.2216 | 0.74356 | 1.0622 | F | 5
| - hereof equipment [%] | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 5
| - hereof installation [%] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 5
| Fixed O&M [M€/GWh Capacity/year] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | G | [1, 5]
| Variable O&M [€/MWhoutput] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | G | [1, 5]
Technology-specific data
| Storage volume for one unit [m3] | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000
| Storage medium | Water | Water | Water | Water | Water | Water | Water | Water | Water | Water
| Max. storage temperature, hot [⁰C] | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
| Storage temperature, discharged [⁰C] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | H
Notes:
A. | The charge/discharge capacity corresponds to an example where a solar fraction of 40% was desired. Other input/output capacities (also relative to storage capacity) may occur for other purposes. Measurements from SUNSTORE 3 show approx. 80% efficiency for a storage with a heat pump.
B. | Values in the table are without a heat pump. The storage loss depends on several parameters, such as storage volume, insulation, whether a heat pump is part of the system etc. Round trip efficiency of approx. 80% when applying a heat pump for cooling to 10°C. (Dis-)charge losses 0 cf. Direct use of water from the connected district heating grid (without heat exchanger). Losses are dependent on the temperature of the storage. 0.08 K/day at average temperature of approx. 78°C, falling to 0.04 K/day at 56°C.
C. | Approx. 100 MWh/year for pumps, at 2,000 fullload hours for the pumps, considering one full cycle pr. year.
D. | Depends on the storage operation temperature profile (seasonal, permanent) temperature in relation to the technical lifetime for liners and insulation. Values stated refer to permanent high temperatures, which means in turn a theoretically unlimited number of cycles.
E. | Excl. extensive planning phase with possible Environmental Impact Assessment etc. Careful timing of steps is mandatory. Depending on the storage size the steps of excavation, building, installation of liners etc. can be done within one summer. For very large volumes the water filling phase can take several months (depending on the filling speed) and filling should preferably be scheduled during the winter. A construction time of approx. 2 years for very large storages is not unrealistic.
F. | Estimated from numerous budget calculations and the cost of the Danish plants, described in the text, and due to effects of economy of scale, the total costs of a PTES in 2020 could be described in a formula: Cost [MEUR] = 1.84 + 42.00*10-6*V, with V being the volume in m3. Corresponding to 69 EUR/m3 at 70,000m3 and 1,06 MEUR/GWh capacity. The costs are based on decent soil conditions, i.e. sand ground and not e.g. heavy clay. The costs can be split as follows: 15% Excavation and reinstallation of soil 35% Bottom and side surfaces & insulation material 20% Installation (of primarily liner) 15% Piping 15% Water (incl. desalination)
G. | The Fixed O&M is set according to capacity of the energy storage specified in the top of the table. Corresponding to approx. 28,000 EUR/storage/year for e.g. divers for inspection, adding of possible leakages and minor fixes.
H. | Cooling to lower temperatures is only possible when a heat pump is used to chill the PTES.
I. | Total efficiency during a one year cycle, including losses during the storage period. The efficiency is very depended on the operation of the storage. E.g. if the yearly efficiency is 80% with one cycle, the same storage will have a yearly efficiency of 90% with two cycles. Examples are: Seasonal without heat pump: 70%, Seasonal with heat pump: up to 90%, and Short-term: 95%.
References:
1. | PlanEnergi, Teknologisk Institut, GEO & Grøn Energi, 2013, Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjernvarmesystemer
5. | PlanEnergi, 2017, based on latest three projects and tender material for two planned PTES (2017/18)
12. | Danish Energy Agency, 1988, Energy Technology Catalogue 38.01
14. | Schmidt, 2018, Monitoring Results from Large Scale Heat storages for District Heating in Denmark. 14th International Conference on Energy Storage, 25-28 April 2018, Adana, Turkey
23. | Sørensen, From, Wetzel, Sifnaios, Jensen [2024] Design, implementation, and monitoring results from the 70,000 m3 pit thermal energy storage (PTES) in Høje Taastrup, Copenhagen - Enerstock Conference, Lyon, France, 5.-7. June 2024
24. | Peham et.al 2024, Lifetime assessment of pit thermal energy storages based on various polyolefinic liner materials

## 141 Large hot water tank
Technology |  | Large-Scale Hot Water Tanks (steel)
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat
| Application | System | System | System | System | System | System | System | System | System
| Energy storage capacity for one unit [MWh] | 175 | 175 | 175 | 175 | 175 | 45 | 315 | 45 | 315 | A
| Output capacity for one unit [MW] | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 0.8 | 5.3 | 0.8 | 5.3 | B | 7
| Input capacity for one unit [MW] | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 0.8 | 5.3 | 0.8 | 5.3 | B | 7
| Round trip efficiency [%] | 98 | 98 | 98 | 98 | 98 | 96 | 99 | 96 | 99 | J | 2
| - Charge efficiency [%] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | C
| - Discharge efficiency [%] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Energy losses during storage [%/day] | 0.18571 | 0.18571 | 0.18571 | 0.18571 | 0.18571 | 0.14286 | 0.24286 | 0.14286 | 0.24286 |  | 2
| Auxiliary electricity consumption [% of output] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | D | 7
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 |  | 7
| Planned outage [weeks/year] | 1 | 1 | 1 | 1 | 1 | 0 | 4 | 0 | 4 | E | 7
| Technical lifetime [years] | 40 | 40 | 40 | 40 | 40 | 30 | 50 | 30 | 50 | F | 2
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 1 | G | 7
Regulation ability
Primary regulation [%/30 sec]
Secondary regulation [%/minute]
Financial data
| Specific investment [M€/GWhCapacity] | 3.0361 | 3.0361 | 3.0361 | 3.0361 | 3.0361 | 2.2112 | 8.177 | 2.2112 | 8.177 | H | [2, 7]
| - hereof equipment [%] | 67.41 | 67.41 | 67.41 | 67.41 | 67.41 | 67.41 | 67.41 | 67.41 | 67.41 |  | 7
| - hereof installation [%] | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 | 28.89 |  | 7
| Fixed O&M [€/MWh Capacity/year] | 8.8069 | 8.8069 | 8.8069 | 8.8069 | 8.8069 | 4.8764 | 34.1351 | 4.8764 | 34.1351 | E | 7
| Variable O&M [€/MWhoutput] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I | 7
Technology-specific data
| Tank volume of example [m3] | 3000 | 3000 | 3000 | 3000 | 3000 | 1500 | 5000 | 1500 | 5000
| Typical temperature difference in storage [hot/cold, K] | 55 | 55 | 55 | 55 | 55 | 30 | 60 | 30 | 60
Notes:
A. Considering a temperature difference of 55K (hot/cold), 90% availability.
B. Considering a full charging cycle of 60 hours (2.5 days), cf. traditional application of steel tanks in Danish DH-plants. The capacity is practically limited by the available pipe dimensions for charge/discharge and the number of installed valves in the tank (in order to increase flow at same low turbulence).
C. As tanks are typically connected directly to the district heating supply/return hydraulic system, there is no loss due to the dis-/charging.
D. Less than 1 % of the stored energy for circulation pumps and N2-production.
E. The Fixed O&M is set according to capacity of the Energy Storage specified in the top of the table. Corresponding to approx. 1500 EUR/tank/year. Typically limited to one inspection/year using a diver, if any at all.
F. Primarily limited by the extent to which the system is held corrosion-free.
G. Installation period for approval by authorities, site preparation, welding, connection, cleansing, initial filling and insulation. Additional delivery time for steel may apply.
H. CAPEX for large-scale water tanks are best described in a formula, due to significant impact of economy of scale. For 2015, the following eqation is used to estimate the CAPEX in EUR pr. m3, based on data as presented in Figure 61.2: 7450*V*^(-0.47), V=Water Volume of tank in m3. Development in CAPEX depends primarily on the development in steel prices.
I. Only variable O&M is electricity consumption for pumps and N2-production as specified above.
J. Total efficiency during a one year cycle, including losses during storage period.
References:
2. PlanEnergi, Teknologisk Institut, GEO & Grøn Energi, 2013, Udredning vedrørende varmelagringsteknologier og store varmepumper til brug i fjern-varmesystemer
7. PlanEnergi, references from various projects in Danish district heating systems.

## 142 Small scale hot water tank
Technology |  | Small-Scale Hot Water Tanks (steel)
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat
| Application | Local | Local | Local | Local | Local | Local | Local | Local | Local
| Energy storage capacity for one unit [kWh] | 3 | 3 | 3 | 3 | 3 | 2 | 19 | 2 | 19 | A
| Output capacity for one unit [kW] | 20 | 20 | 20 | 20 | 20 | 10 | 40 | 10 | 40 |  | 5
| Input capacity for one unit [kW] | 20 | 20 | 20 | 20 | 20 | 10 | 40 | 10 | 40 |  | 5
| Round trip efficiency [%] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | J
| - Charge efficiency [%] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | B
| - Discharge efficiency [%] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
| Energy losses during storage [%/hour] | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.5 | 1 | 2.5 | 1 | I
| Auxiliary electricity consumption [% of output] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | C
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 3 |  | 5
| Planned outage [weeks/year] | 1 | 1 | 1 | 1 | 1 | 0 | 4 | 0 | 4 | D
| Technical lifetime [years] | 30 | 30 | 30 | 30 | 30 | 15 | 50 | 15 | 50 | E | 5
| Construction time [years] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F | 6
Regulation ability
Primary regulation [%/30 sec]
Secondary regulation [%/minute]
Financial data
| Specific investment [€/kWh] | 419.8622 | 419.8622 | 419.8622 | 419.8622 | 419.8622 | 522.2676 | 133.127 | 522.2676 | 133.127 | [F, G, L] | [5, 6]
| - hereof equipment [%] | 48.15 | 48.15 | 48.15 | 48.15 | 48.15 | 38.52 | 33.705 | 38.52 | 33.705 |  | 6
| - hereof installation [%] | 49.9316 | 49.9316 | 49.9316 | 49.9316 | 49.9316 | 59.2052 | 63.8421 | 59.2052 | 63.8421 |  | 6
| Fixed O&M [€/tank/year] | 51.2027 | 51.2027 | 51.2027 | 51.2027 | 51.2027 | 25.6014 | 81.9243 | 25.6014 | 81.9243 | D | [5, 6]
| Variable O&M [€/MWh] | 0.61443 | 0.71684 | 1.0241 | 1.2289 | 1.2289 | 0 | 0.71684 | 0 | 1.2289 | H | 6
| - of which is electricity costs [€/MWh] | 0.61443 | 0.71684 | 1.0241 | 1.2289 | 1.2289 | 0 | 0.71684 | 0 | 1.2289 | K
| - of which is other O&M costs [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Technology-specific data
| Efficiency at typical cycle period [%] | 92 | 92 | 92 | 92 | 92 | 97 | 90 | 97 | 90 | [I, B]
| Tank volume of example [l] | 90 | 90 | 90 | 90 | 90 | 50 | 300 | 50 | 300
| Typical temperature difference in storage [hot/cold, K] | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 30 | 60 | A | 8
Notes:
A. Considering a temperature difference of 30K (hot/cold), cf. DS12897:2016 [8], and 60K for large tanks, typically for solar thermal applications.
B. As tanks are typically connected directly to the hydraulic heating system of a building, there is no loss due to the dis-/charging. The heat loss of the tank will typically be utilised as spatial heating, if the tank is mounted inside the building.
C. Less than 1 % of the stored energy for circulation pumps.
D. Typically limited to replacement of the anode for every 3 years, potentially the control unit or valves and fittings.
E. Primarily limited by the extent to which the system is held corrosion-free (the enamelling is held undamaged).
F. Installation period assessed to be 3-8 hours each for two skilled workers, i.e. the construction site is cleared/prepared, varying by the tank size.
G. CAPEX cf. a stand-alone cabinet-solution, mounted, site-clearance/preparation and removal of existing heating source/storage not included. Cost for fittings etc. approx. 10 % of total CAPEX. Additional investment for electric heater of approx. 100 EUR may be added if necessary.
H. Only variable O&M is electricity consumption for pumps as specified above.
I. Considering a heat loss of 60 W at temperature 65/35°C in the storage and 20°C ambient for the 90 l unit. Considering an idle/discharging cycle of total 4 hours.
J. Round trip efficiency is not applicable for seasonal storage.
K. The cost of auxiliary electricity consumption is calculated using the following electricity prices in EUR/MWh: 2015: 63, 2020: 69, 2030: 101, 2040: 117, 2050: 117. These prices include production costs and transport tariffs, but not any taxes or subsidies for renewable energy.
L. CAPEX is related to storage volume. I.e. an increase of temperature difference in storage yields a lower specific investment/MWh.
References:
5. Metro-Therm A/S, 2019, sales department and homepage.
6. PlanEnergi, 2019
8. Danish standard, "Specification for indirectly heated unvented (closed) storage water heaters", DS12897:2016

## 143a Rock-based Carnot battery
Technology |  | Carnot battery
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat
| Application | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | Heat or steam for industry or district heating | A,B
| Energy storage capacity for one unit [MWh) | 300 | 300 | 300 | 300 | 300 | 100 | 500 | 100 | 500 | C
| Output capacity for one unit [MW] | 10 | 10 | 10 | 10 | 10 | 5 | 50 | 5 | 50 | C
| Input capacity for one unit [MW] | 15 | 15 | 15 | 15 | 15 | 5 | 50 | 5 | 50 | C
| Round trip efficiency PtP [%] | 10 | 10 | 10 | 10 | 10 | 5 | 15 | 5 | 15 | D
| System efficiency PtH [%] | 95.04 | 95.04 | 95.04 | 95.04 | 95.04 | 91.14 | 96.03 | 91.14 | 96.03
| - Charge efficiency [%] | 99 | 99 | 99 | 99 | 99 | 98 | 99 | 98 | 99 | E
| - Discharge efficiency [%] | 96 | 96 | 96 | 96 | 96 | 93 | 97 | 93 | 97 | F
| Energy losses during storage [%/day] | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.14286 | 0.09 | 0.11 | 0.09 | 0.11 | G
| Auxiliary electricity consumption [% of output] | 4.5 | 4.275 | 4.0612 | 3.8582 | 3.4724 | 4.05 | 4.95 | 3.1251 | 3.8196 | H
Forced outage [%] | bar: -
Planned outage [weeks/year] | bar: -
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | J
| Construction time [years] | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 2 | 1 | 2
Regulation ability
| Primary regulation [%/30 sec] | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | K, L
| Secondary regulation [%/minute] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | K, L
Financial data
| Specific investment [k€/MWh Capacity] | 13.0481 | 12.3956 | 11.7759 | 11.1871 | 10.0684 | 5.655 | 18.096 | 4.3636 | 13.9636 | M, Q
| Specific investment Output Capacity [k€/MW Capacity] | 30.1109 | 28.6053 | 27.1751 | 25.8163 | 23.2347 | 13.05 | 41.76 | 10.0699 | 32.2236 | N, Q
| Specific investment Input Capacity [k€/MW Capacity] | 120.4435 | 114.4214 | 108.7003 | 103.2653 | 92.9388 | 52.2 | 167.04 | 40.2795 | 128.8943 | M, Q
| - hereof equipment [%] | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| - hereof installation [%] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Fixed O&M [€/MWh Capacity/year) | bar: -
Variable O&M [€/MWh output] | bar: -
Technology-specific data
| Tank volume of example [m3] | 3000 | 3000 | 3000 | 3000 | 3000 | 1000 | 5000 | 1000 | 5000 | O
| Typical temperature difference in storage | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | P
Notes:
A | Process heat in the range 150C-250C. A turbine loop can be integrated to improve business case by selling electricity and turbine related auxillary services, the waste heat from the turbine could be used for district heating.
B | Process heat for industry / heat for district heating and electricity generation via TES load shifting. Combined power-to-heat and power-to-power.
C | Storage, input and output capacity can be dimensioned to fit to a particular installation, these are typical design values
D | In a power-to-power scenario, the excess energy can be used for process heat or district heating leading to system effiencies above 90%
E | Charging by resistive heating elements
F | Based on a scenario where the heat is stored for several weeks.
G | Energy loses: A small amount is lossed through the insulation. Around 1% per week.
H | Auxiliary electricity consumption: Estimates on mainly pump consumption
I | No reliable data found
J | Large uncertainty in indicated value. Pumps and other components will need replacement periodically within this time frame. Estimates based on comparable installations in other fields
K | If system is hot the charging can go to 100% heating per minute.
L | If a turbine is included, the generatotion capacity should be added
M | Does not include costs for power connection to the grid (high voltage line , transformerstation etc.) Is does also not include cost for preparation of building site.
N | Does not include cost for turbine / generator and systems for DH integration of turbine waste heat
O | Tank volume: is the collected tank volumes so that it fits the indicated capacity
P | Typical temperature difference in storage: [hot/cold, K] 75-300. Depends on the temperature of the heat load and storage temperature, values here are indicated for fluid based heat transfer from storage, e.g. thermal oils
Q | Deflated to 2020 prices from 2024 by multiplying by 0.87 based on https://www.dst.dk/da/Statistik/emner/oekonomi/prisindeks/forbrugerprisindeks
References:
Based on market survey and litterature study carried out by Teknologisk Institut 2024

## 143b Molten salt Carnot battery
Technology |  | Carnot battery
year |  | 2025 | 2030 | 2035 | 2040 | 2050 | 2025 | 2025 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat | Heat
| Application | Industrial steam | Industrial steam | Industrial steam | Industrial steam | Industrial steam | Industrial steam | Industrial steam | Industrial steam | Industrial steam | A
| Energy storage capacity for one unit [MWh) | 200 | 800 | 800 | 800 | 800 | 100 | 200 | 100 | 1000 | B
| Output capacity for one unit [MW] | 12 | 50 | 50 | 50 | 50 | 10 | 100 | 10 | 100 | B
| Input capacity for one unit [MW] | 30 | 120 | 120 | 120 | 120 | 10 | 120 | 10 | 120 | B
| Round trip efficiency PtP [%] | 30 | 30 | 30 | 30 | 30 | 10 | 40 | 10 | 40 | C
| System efficiency PtH [%] | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | D
| - Charge efficiency [%] | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | E
| - Discharge efficiency [%] | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Energy losses during storage [%/day] | bar: ctrl to Upper
Auxiliary electricity consumption [% of input] | bar: ctrl to -
| Forced outage [%] | 5 | 4 | 3 | 2 | 2 | 3 | 15 | 1 | 5 | G
| Planned outage [weeks/year] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Technical lifetime [years] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | H
| Construction time [years] | 1 | 1 | 1 | 1 | 1 | 0.5 | 1.5 | 0.5 | 1.5
Regulation ability
| Primary regulation [%/30 sec] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | I, J
| Secondary regulation [%/minute] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | I, J
Financial data
| Specific investment [KEUR2020/MWhCapacity] | 92.22 | 62.7096 | 55.332 | 48.8224 | 38.0105 | 76.125 | 108.75 | 31.3766 | 51.5215 | K,G, N
| - hereof equipment [%] | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | L, G
| - hereof installation [%] | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | M, G
| Fixed O&M [% of Total investment/year) | 2 | 1.5 | 1.5 | 1 | 1 | 1 | 3 | 0.5 | 2 | G
| Variable O&M [% of Total investement/year] | 2 | 1.5 | 1.5 | 1.5 | 1.5 | 1 | 3 | 0.05 | 2.5 | G
Technology-specific data
| Tank volume of example [m3] | 500 | 3000 | 3000 | 3000 | 3000 | 400 | 500 | 400 | 4000 | N
| Typical temperature difference in storage [hot/cold, K] | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
| Steam temperature [°C] | 250 | 250 | 250 | 250 | 250 | 250 | 550 | 250 | 550
| footprint of plant [m2] | 800 | 1500 | 1500 | 1500 | 1500 | 400 | 500 | 400 | 1700
| hours of discharge [hours] | 24 | 24 | 24 | 24 | 24 | 3 | 24 | 3 | 24
Notes:
A | A turbine generator can be included to produce electricity and widen ancillary services capabilties, see technology catalogue on power and heat producing technologies for data on CHPs
B | Storage, input and output capacity can be dimensioned to fit to a particular installation, these are typical design values
C | In a power-to-power scenario, the excess energy can be used for process heat or district heating leading to system effiencies above 90%
D | Assumes 0,75% loss from storage period (24-48 hours)
E | Charging by resistive heating elements
F | Mainly pumping power and loss of heat to environment
G | Large uncertainty in indicated value
H | Large uncertainty in indicated value. Pumps and other components will need replacement periodically within this time frame. Estimates based on comparable installations in other fields
I | Requires hot system
J | Upregulation only possible when charging
K | Local grid connection and grid reinforcements not included
L | Equipment is all major pieces of equipment, e.g. pumps, heaters etc.
M | Installation includes all costs that are not major pieces of equipment including EPC costs
N | Deflated to 2020 prices from 2024 by multiplying by 0.87 based on https://www.dst.dk/da/Statistik/emner/oekonomi/prisindeks/forbrugerprisindeks
Notes: | Small dead space in the bottom of tank limits full use of volume to store usefull energy
References:
Based on market survey and litterature study carried out by Teknologisk Institut 2024

## 150 Underground Storage of Gas
Technology |  | Natural gas storage underground
year |  | 2020 | 2030 | 2040 | 2050 | Note | Ref | Explanation
est |  | ctrl | ctrl | ctrl | ctrl | - | - | -
cat | par
Energy/technical data
| Form of energy stored | Chemical | Chemical | Chemical | Chemical
| Application | System | System | System | System |  |  | Systemorlocal(ifelectricityspecifyalsoifpowerintensiveorenergyintensive)
| Energy storage capacity for one unit [MWh] | 1100 | 1100 | 1100 | 1100
| Output capacity for one unit [MW] | 6600 | 6600 | 6600 | 6600
| Input capacity for one unit [MW] | 2200 | 2200 | 2200 | 2200
Financial data
| Specific investment [M€/MWh] | 0.00023656 | 0.00023656 | 0.00023656 | 0.00023656
| Installation, equipment, manhours [M€/MWh] | 2.6067e-06 | 2.6067e-06 | 2.6067e-06 | 2.6067e-06
| Fixed O&M [€/MW/year] | 1.2698 | 1.2698 | 1.2698 | 1.2698
| Variable O&M [€/MWh] | - | - | - | -
Technology-specific data
| Plant for cavern leaching [M€] | 10.5277 | 10.5277 | 10.5277 | 10.5277
| Construction work [M€] | 2.9951 | 2.9951 | 2.9951 | 2.9951 | A
| Compressors, incl. Auxiliaries [M€] | 32.0479 | 32.0479 | 32.0479 | 32.0479 | A
| Udtrækstog [M€] | 13.7776 | 13.7776 | 13.7776 | 13.7776 | A
| Withdrawal equipment [M€] | 4.7922 | 4.7922 | 4.7922 | 4.7922 | A
| Connections, transformer, regulation, and instruments [M€] | 13.4781 | 13.4781 | 13.4781 | 13.4781 | A
| Total investment cost [M€] | 67.0909 | 67.0909 | 67.0909 | 67.0909 | A
| Construction and equipment [M€] | 23.5118 | 23.5118 | 23.5118 | 23.5118 | B
| Cushion gas for one cavern (40% of total) [M€] | 14.9757 | 14.9757 | 14.9757 | 14.9757 | B
| Total cost [M€] | 38.4874 | 38.4874 | 38.4874 | 38.4874 | B
Notes:
A. Process equipment; injection 200,000 Nm3/hour (approx. 2200 MW), withdrawal 600,000 nM3/hour (approx. 6600 MW)
B. Establishment of one cavern, 100 million Nm3 (approx. 1.1 TWh)
C. A new greenfield store, equivalent to Lille Torup in Denmark, would require one leaching plant, 5 caverns, and one process plant.
D. Total investment cost
References:
<none>

## 151a Hydrogen Storage - Tanks
Technology |  | Pressurized hydrogen gas storage system (Compressor & Type I tanks @ 200bar)
year |  | 2019 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref | Explanation
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | - | -
cat | par
Energy/technical data
| Form of energy stored | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical
| Application | Local | Local | Local | Local | Local | Local | Local | Local | Local | L |  | System or local (if electricity specify also if power intensive or energy intensive)
| Energy storage capacity for one unit [MWh] | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 |  | 1
Output capacity for one unit [MW] | bar: ctrl to -
| Input capacity for one unit [MW] | 0.1 | 0.095 | 0.09 | 0.08 | 0.08 | 0.1 | 0.99 | 0.085 | 0.08 | B | [1, 2]
| Round trip efficiency [%] | 88.29% | 88.29% | 88.96% | 89.65% | 90.24% | 88.29% | 88.29% | 89.75% | 90.24% | C | 1
| - Charge efficiency [%] | 88.29% | 88.29% | 88.96% | 89.65% | 90.24% | 88.29% | 88.29% | 89.75% | 90.24% | D
| - Discharge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | E
| Energy losses during storage [%/period] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | F, K
| Auxiliary electricity consumption [% of output] | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | J |  | Expressed only for heat and gas storages
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I
| Planned outage [weeks/year] | 3 | 3 | 2 | 1.5 | 1 | 3 | 3 | 1.5 | 0.5 | G | 3
| Technical lifetime [years] | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 30 | 30
| Construction time [years] | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 |  | 3
Regulation ability |  | -: Only for electricity storage
| Primary regulation [%/30 sec] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | H | 3
| Secondary regulation [%/minute] | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | H | 3
Financial data
| Specific investment [M€/MWh] | 0.060614 | 0.060614 | 0.047757 | 0.028765 | 0.022331 | 0.060614 | 0.060614 | 0.037485 | 0.022331 |  | 1
| Compressor component [M€/MWh] | 0.031902 | 0.031902 | 0.025443 | 0.013528 | 0.0084811 | 0.031902 | 0.031902 | 0.016962 | 0.0084811 |  | 1
| Type I tanks component [M€/MWh] | 0.019141 | 0.019141 | 0.016894 | 0.011857 | 0.010177 | 0.019141 | 0.019141 | 0.015266 | 0.010177 |  | 1
| Installation, equipment, manhours [M€/MWh] | 0.0095706 | 0.0095706 | 0.0084472 | 0.0067171 | 0.0050887 | 0.0095706 | 0.0095706 | 0.007633 | 0.0050887 |  | 1
| Fixed O&M [€/MW/year] | 638.04 | 638.04 | 531.7 | 531.7 | 425.36 | 638.04 | 638.04 | 478.53 | 319.02 |  | 1
Variable O&M [€/MWh] | bar: ctrl to Upper
Technology-specific data |  | -: See table in the specific section
| Gravimetric energy density [kWh/kg] | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
| Volumetric energy density @0oC and 1atm pressure [kWh/m3] | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09
| Permeation characteristics for Type I tanks [mol/s/m/MPa1/2] | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 | 2.84×10-27 |  | 4
Notes:
A. Cannot be defined since there is no conversion of hydrogen back to electricity in the form of a fuel cell in the system
B. The only power input that is considered is the input for the compressor and does not include power needs for the electrolyzer that is making the hydrogen as described in the system definition. Compressor power input decrease of 5% every 10 years
C. Calculated in the "Energy Efficiency" section. Compressor efficency lineraly improved by 20% until 2050.
D. The charge efficiency is practically the roundrtip efficiency itself as there are almost no losses in the discharge process (See note E)
E. Almost no losses during discharge as it is a physical discharge for a pressurized gas from a valve.
F. Permeation characteristics are neglibile for Type I tanks, see also Technology-specific data.
G. System O&M includes maintenance of the compressor and periodic check of the tanks intergrity.
H. System complies with the frequency regulation requirements from Energinet
I. No hydrogen storage systems are known to have time of forced outage.
J. Compressor consumption is not considered auxiliary. Rest of losses that can be translated into energy losses and consequently more electricity consumption are negligible.
K. Losses are below <1%
L. Stationary short-medium term storage after production from an electrolyzer
References:
<none>

## 151b Hydrogen Storage - LOHC
Technology |  | Hydrogen storage - LOHC
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref | Explanation
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | - | -
cat | par
Energy/technical data
| Form of energy stored | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical |  |  | Electricity, heat or gas
| Application | -: System or local (if electricity specify also if power intensive or energy intensive)
| Energy storage capacity for one unit [MWh] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | A
| Output capacity for one unit [MW] | 0.1 | 2 | 5 | 10 | 50 | - | - | - | -
| Input capacity for one unit [MW] | 0.3 | 7 | 34 | 70 | 300 | 2 | 2 | 50 | 500 | B
| Round trip efficiency [%] | 72% | 72% | 74% | 75% | 75% | 75% | 75% | 75% | 75% | C | 47
| - Charge efficiency [%] | ctrl: 72%; ctrl: 72%; ctrl: 74%; ctrl: 75%; ctrl: 75%; -: I
| - Discharge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 47
| Energy losses during storage [%/period] | 1% | 1% | 1% | 1% | 1% | 0% | 1% | 0% | 1% |  | 9 | Loss is time independent
| Auxiliary electricity consumption [% of output] | 1% | 1% | 1% | 1% | 1% | 0% | 1% | 0% | 1% |  |  | Expressed only for heat and gas storages
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Planned outage [weeks/year] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 47
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 47
Construction time [years] | bar: ctrl to Upper
Regulation ability
Primary regulation [%/30 sec] | bar: ctrl to ctrl; -
Secondary regulation [%/minute] | bar: ctrl to ctrl
Financial data
| Specific investment [M€/MWh] | 0.00089326 | 0.00089326 | 0.0005317 | 0.00047853 | 0.00042536 | 0.00089326 | 0.00089326 | 0.00042536 | 0.00031902 | E |  | Investment/MWh is not a relevant factor for the LOHC technology as MW and MWh our fully independet, thus the full investment/MWh depends on the specific case. Therefore I also cannot follow/understand your numbers.
| - hereof equipment [M€/MWh] | 0.0005317 | 0.0005317 | 0.00031902 | 0.00030532 | 0.00025522 | 0.0005317 | 0.0005317 | 0.00025522 | 0.00019141 | F
| - hereof installation [M€/MWh] | 0.00036156 | 0.00036156 | 0.00021268 | 0.00019141 | 0.00017014 | 0.00036156 | 0.00036156 | 0.00017014 | 0.00012761 | F
| Fixed O&M [€/MW/year] | 3.7996e-05 | 3.7996e-05 | 2.2616e-05 | 2.0355e-05 | 1.8093e-05 | 3.7996e-05 | 3.7996e-05 | 1.8093e-05 | 1.357e-05 | G
| Variable O&M [€/MWh] | 9.4989e-06 | 9.4989e-06 | 5.6541e-06 | 5.0887e-06 | 4.5233e-06 | 9.4989e-06 | 9.4989e-06 | 4.5233e-06 | 3.3925e-06 | H
Technology-specific data |  | -: See table in the specific section
| Specific energy [Wh/kg] | 2080 | 2080 | 2080 | 2080 | 2080 | 2080 | 2080 | 2080 | 2080 |  | 43
| Energy density [kWh/m3] | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 |  | 43
Notes:
A. Calculated based on techno-economic data of 12tpd plant from Hydrogenious
B. Losses during hydrogenation
C. Efficiency as received from Hydrogenious
D. LOHC uptake does not change with part load operation
E. Investment cost on the lines of 5500 tpd scenario.
F. Assuming 60% as equipment cost and 40% as installation cost
G. Fixed O&M is treated at 4% of CAPEX (Data obtained from hydrogenious)
H. Variable O&M is treated as 1% of CAPEX
I. Input and Outpu tefficiency are exactly the other way round (i, e, output at 72%)
References:
<none>

## 151c Hydrogen Storage - Caverns
Technology |  | Hydrogen storage - caverns
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref | Explanation
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | - | -
cat | par
Energy/technical data
| Form of energy stored | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical | Chemical |  |  | [Electricity, heat or gas]
| Application | Local | Local | Local | Local | Local | Local | Local | Local | Local |  |  | System or local (if electricity specify also if power intensive or energy intensive)
| Energy storage capacity for one unit [MWh] | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | 150000 | A | 54-57
Output capacity for one unit [MW] | bar: ctrl to Upper
| Input capacity for one unit [MW] | 180 | 175 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | B | 54-57
| Round trip efficiency [%] | 99% | 99% | 99% | 99% | 99% | 99% | 99% | 99% | 99% |  | 54-57
| - Charge efficiency [%] | 99% | 99% | 99% | 99% | 99% | 98% | 99% | 99% | 99% |  | 54-57
| - Discharge efficiency [%] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | 54-57
| Energy losses during storage [%/period] | 1% | 1% | 1% | 1% | 1% | 0% | 1% | 0% | 1% | C
| Auxiliary electricity consumption [% of output] | 1% | 1% | 1% | 1% | 1% | 0% | 1% | 0% | 1% |  |  | Expressed only fo rheat and gas storages
Forced outage [%] | bar: ctrl to Upper
Planned outage [weeks/year] | bar: ctrl to -
| Technical lifetime [years] | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 57
Construction time [years] | bar: ctrl to -
Regulation ability |  | -: Only for electricity storage
| Primary regulation [%/30 sec] | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | F
| Secondary regulation [%/minute] | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Financial data
| Specific investment [M€/MWh] | 0.0031902 | 0.0031902 | 0.0021268 | 0.0015951 | 0.0012761 | 0.0031902 | 0.0031902 | 0.0019141 | 0.0010634 |  | 59
| - hereof equipment [M€/MWh] | 0.00095706 | 0.00095706 | 0.00063804 | 0.0005317 | 0.00042536 | 0.00095706 | 0.00095706 | 0.00095706 | 0.00095706 |  | 59
| - hereof installation [M€/MWh] | 0.0019141 | 0.0019141 | 0.0012761 | 0.00095706 | 0.00074438 | 0.0019141 | 0.0019141 | 0.0019141 | 0.0019141 |  | 59
| Fixed O&M [€/MW/year] | 6.7849e-05 | 6.7849e-05 | 4.5233e-05 | 3.3925e-05 | 2.714e-05 | 6.7849e-05 | 6.7849e-05 | 4.071e-05 | 2.2616e-05 | G | 57
| Variable O&M [€/MWh] | 3.6075e-05 | 3.6075e-05 | 2.405e-05 | 1.8038e-05 | 1.443e-05 | 3.6075e-05 | 3.6075e-05 | 2.1645e-05 | 1.2025e-05 | H
Technology-specific data |  | -: See table in the specific section
| Gravimetric energy density [Wh/kg] | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | I
Volumetric energy density @0oC and 1atm pressure [Wh/m3] | bar: -
Permeation characteristics [mol/s/m/MPa1/2] | bar: ctrl to -
Notes:
A. Data calculated according to the system defined in the report
B. Based on system definition
C. Negligible energy losses reported in literature
D. One constructed, no outage time is defined
E. Pre existing caverns
F. Regulation similar to the tanks based on demand supply profile
G. O&M cost defined as a percentageof CAPEX in litertaure
H. Variable O&M is treated as half of fixed O&M
I. Only considering hydrogen pressure, not considering gradient in the cavern (since it depends on the site)
J. Negligible permeation losses (Through conversations with Gas energy denmark)
References:
<none>

## 160 Pumped hydro storage
Technology |  | Pumped hydro storage
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical
| Generating capacity for one unit [MW] | 500 | 500 | 500 | 500 | 10 | 1000 | 10 | 1000 | A | 2
| Total efficiency [%] net | 75 | 75 | 75 | 75 | 70 | 80 | 70 | 80 | A | 1
| Technical lifetime [years] | 50 | 50 | 50 | 50 |  |  |  |  | A | 1
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 | A
Financial data
| Investment, pump part [M€/MW] | 0.63804 | 0.63804 | 0.63804 | 0.63804 | 0 | 0 | 0 | 0 | [B, C, A] | 1&2
| Investment, total, greenfield plant [M€/MW] | 4.2536 | 4.2536 | 4.2536 | 4.2536 | 0 | 0 | 0 | 0 | [D, A] | 4
| Fixed O&M [€/MW/year] | 8507.2 | 8507.2 | 8507.2 | 8507.2 | 6380.4 | 12760.8 | 6380.4 | 12760.8 | [B, A] | 3
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
References:
1. BKK, presentation on Nygard Pumpekraftverk
2. Tonstad Pumpekraftverk, Sira-Kvina kraftselskap, 2002
3. BKK and Sira-Kvina (1-2% of investment)
4. “Energy technology perspectives 2008”, International Energy Agency, 2008.
Notes:
A. No significant technology advance or cost decrease is expected, since hydropower and water pumping are established technologies.
B. Based on the September 2004 exchange rate of 1NOK = 0,12EUR
C. Cost data are the same as in the 2005 catalogue, however inflated from price level 2002 to 2011 by multiplying with a general inflation factor 1.2306
D. Cf. paragraph 'Additional remarks' above.

## 161 CAES
Technology |  | Compressed Air Energy Storage
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical
| Application | System, energy-intensive | System, energy-intensive | System, energy-intensive | System, energy-intensive | System, energy-intensive | System, energy-intensive | System, energy-intensive | System, energy-intensive
| Energy storage capacity for one unit [MWh] | 3000 | 3000 | 3000 | 3000 | - | - | 3000 | 10000 | I | [3]
| Output capacity for one unit [MW] | 300 | 300 | 300 | 300 | - | - | 300 | 500 | I, J | [3]
| Input capacity for one unit [MW] | 60 | 60 | 60 | 60 | - | - | 60 | 80 | I, J | [9]
| Round trip efficiency [%] | 55 | 60 | 70 | 72 | 55 | 55 | 64 | 72 | A, B | [9] [26]
| - Charge efficiency [%] | 80 | 80 | 84 | 85 | 80 | 80 | 80 | 85 |  | [7]
| - Discharge efficiency [%] | 69 | 80 | 84 | 85 | 69 | 69 | 80 | 85 |  | [7]
| Energy losses during storage [%/period] | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | [27]
Auxiliary electricity consumption [% of output] | bar: ctrl to ctrl
| Forced outage [%] | 5 | 5 | 4 | 4 | - | - | 2 | 4 | I, K | [9]
| Planned outage [weeks/year] | 5 | 5 | 4 | 3 | - | - | 2 | 3 | I, K | [9]
| Technical lifetime [years] | 40 | 40 | 40 | 40 | 35 | 45 | 35 | 45 |  | [20] [8]
| Construction time [years] | 2.5 | 2.5 | 2.5 | 2.5 | 2 | 3 | 2 | 3 |  | [8]
Regulation ability
| Idle to full discharge [sec] | 700 | 700 | 1000 | 1000 | 500 | 1000 | 800 | 1200 | D, G | [3], [8]
Full charge to full discharge [sec] | bar: ctrl to ctrl; -
Financial data
| Specific investment [M€/MWh] | 0.69121 | 0.69121 | 1.0634 | 0.85072 | 0.31902 | 1.2761 | 0.42536 | 2.1268 | C, E | Table 3 [26]
| - Energy component [M€/MWh] | 0.0021268 | 0.0021268 | 0.0021268 | 0.0021268 | 0.0021268 | 0.010634 | 0.0021268 | 0.010634 | H | [23]
| - Capacity component [M€/MW] | 0.63804 | 0.63804 | 0.95706 | 0.95706 | 0.31902 | 1.2761 | 0.31902 | 1.2761 | 0 | [24]
| - Other project costs [M€/MWh] | 0.090389 | 0.090389 | 0.090389 | 0.090389 | 0.085072 | 0.095706 | 0.085072 | 0.095706 | 0 | [24]
| Fixed O&M [€/MW/year] | 2615.964 | 2615.964 | 2615.964 | 2615.964 | 2126.8 | 4253.6 | 2126.8 | 4253.6 | 0 | [20]
| Variable O&M [€/MWh] | 2.616 | 2.616 | 2.616 | 2.616 | 2.1268 | 3.1902 | 2.1268 | 3.1902 | 0 | [20]
Technology-specific data
| Specific investment [€/kW] | 680.576 | 680.576 | 680.576 | 680.576 | - | - | 584.87 | 680.576 | C, K | Table 3
Notes:
A. For efficiency it is assumed that that new CAES plants can be constructed with at least the same efficiency as the McIntosh plant.
B. The use of gas in a CAES plant is assumed at the same efficiency as the average use of chemical fuels in the Danish electricity system, i.e. 35% in 2014
C. In general it is assumed that at some point between 2020 and 2030 adiabatic CAES plants will dominate the market. This means that investment costs will increase and performance characteristics will improve.
D. The obtainable ramping rate is likely to decrease after application of thermal energy storage. This is because the heat must be delivered to the storage material, which is a process that cannot be controlled independently.
E. For the costs/kWh in Table 3 the data lying between 0 and 2 EUR/kWh have been disregarded because it is assumed, that only storage costs are included
F. Operation not suitable nor relevant for CAES. Data not available.
G. If a CAES plant is operated as a hot spinning reserve, it can reach the maximum capacity within a few minutes. The emergency startup times from cold conditions at the Huntorf and McIntosh plants are about 5 minutes. Their normal startup times are about 10 to 12 minutes [8]
H. Energy component here taken as the cavern excavating
I. New plants cannot be realized in 2020 because of lead time. Furthermore the upper limit for storage capacity of one unit is determined by cavern volume, which can be obtained practically without.
J. Upper limit in 2050 is based on the author´s assessment of technological development until then.
K. Lower limit in 2050 is based on the author´s assessment of technological development until then.
References:
1. S. Karellas and N. Tzouganatos, "Comparison of the performance of compressed-air and hydrogen," vol. 29, 2014.
2. E. Barbour, "http://energystoragesense.com/compressed-air-energy-storage/," [Online].
3. S. Zunft, S. Freund and E. M. Schlichtenmayer, "Large Scale Electricity Storage with Adiabatic CAES," Paris, November 2014.
4. "Geological storage in Northern Ireland," Geological Survay of Northern Ireland. [Online].
5. P. Johnson, "ASSESSMENT OF COMPRESSED AIR ENERGY STORAGE SYSTEM (CAES)," Thesis Submitted to the University of Tennessee, University of Tennessee at Chattanooga, Chattanooga, Tenessee, USA, 2014.
6. R. W. S. Succar, "Compressed Air Energy Storage: Theory, Resources, And Applications For Wind Power," Energy Systems Analysis Group, Princeton Environmental Institute, Princeton University, April 2008.
7. J. W. X. Luo, "Overview on current development on Compressed Air Energy Storage, EERA Technical Report – CAES.," School of engineering, University of Warwick. Available on http://integratedenergystorage.org/. Accessed February 2017, December 2013.
8. I. Gyuk and S. Eckroad, "EPRI-DOE Hanbook of Energy Storage for Transmission and Distribution Applications,1001834, Final Report," EPRI and DOE, December 2003.
9. Nakhamkin and Brotel, "Second generation compressed air storage," in Energy Storage Forum Europe, Rome, 2012.
10. F. Crotogino, K.-U. Mohmeyer and R. Scharf, "Huntorf CAES/More than 20 yeasr of successful operation," Orlando, April 2001.
11. "https://dddusmma.wordpress.com/2014/05/30/storage-is-essential-for-wind-and-solar/," Department of Energy, USA. [Online]. [Accessed 2017].
12. "https://dddusmma.wordpress.com/2015/03/17/the-quest-for-storing-electricity/," 17 March 2015. [Online]. [Accessed 2017].
13. A. Wänn, P. Leahy, M. Reidy, S. Doyle, H. Dalton and P. Barr, "Environmental performance of existing energy storage installations. Deliverable D.3.1. Available on www.store-project.eu. Accessed February 2017," stoRE project, 2012.
14. E. Bouman, M. M. Øberg and E. G. Hertwich, "LIFE CYCLE ASSESSMENT OF COMPRESSED AIR ENERGY STORAGE (CAES)," Gothenburg, 2013.
15. "ADELE – ADIABATIC COMPRESSED-AIR ENERGY STORAGE FOR ELECTRICITY SUPPLY. RWE Brochure.," RWE Power AG, Cologne, 2010.
16. "Energy Storage Technology Roadmap, Technology Annex, p. 5," International Energy Agency, March 2014.
17. Gaelectric. Accesses February 2017. [Online].
18. "Gaelectric energy storage: The missing link. Brochure by Gaelectric. Availble on http://www.gaelectric.ie/energy-storage-publications/. Accessed February 2017," Gaelectric.
19. [Online].
20. D.Rastler, A. Akhil and D. Gauntlett, "Energy Storage System Costs 2011 update. Excecutive summary.," 2011.
21. "InflationData.com," InflationData, 2017. [Online]. [Accessed March 2017].
22. E. Drury, P. Denholm and R. Sioshansi, "The Value of Compressed Air Energy Storage in Energy and Reserve Markets," National Renewable Energy Laboratory, USA, 2009.
23. "Handbook for Energy Storage for Transmission or Distribution Applications. Report No. 1007189. Technical Update December 2002. Document can be found at: www.epri.com," EPRI, 2002.
24. "COST AND PERFORMANCE DATA FOR POWER GENERATION TECHNOLOGIES, Report prepared for the National Renewable Energy Laboratory, Avaliable on https://www.bv.com/docs/reports-studies/nrel-cost-report.pdf (Accessed February 2017)," Black & Veatch, 2012.
25. B. McGrail, "Techno-economic Performance Evaluation of Compressed Air Energy Storage in the Pacific Northwest. Available on http://caes.pnnl.gov/pdf/PNNL-22235.pdf. Accessed February 2017," Pacific Northwes National Laboratory (operated by Batelle), 2013.
26. "Materials Roadmap Enabling Low Carbon Energy Technologies, Commission Staff Working Paper," European Commission, Brussels, 2011.
27. A. Bary, "Storing natural gas underground. Available on https://www.slb.com/~/media/Files/resources/oilfield_review/ors02/sum02/p2_17.pdf (Accessed February 2017)," Oilfield review, 2002.
28. A. Cavallo, "Controllable and affordable utility-scale electricity from intermittent wind resources and compressed air energy storage (CAES)," vol. 32, pp. 120-127, 2007.
29. J. T. Dasand, "Compressed Air Energy Storage (Educational Chapter)," Iowa state University, 2012.
30. E. M. G.Locatellia, "Assessing the economics of large Energy Storage Plants with an optimisation methodology," vol. 83, April 2015.
31. "Energy Storage News," Energy Storage News, 2016. [Online].
32. P. Tayler, "Pathways for Energy Storage in the UK, Report 007," The Centre for Low Carbon Futures, March 2012.
33. H. Lund and G. Salgi, "The role of compressed air energy storage (CAES) in future sustainable energy systems," vol. 50, pp. 1172-1179, 2009.
34. M. Nakhamkin, M. Chiruvolu and C. Daniel, "Available Compressed Air Energy Storage (CAES) Plant Concepts. Available on http://www.espcinc.com/library/PowerGen_2007_paper.pdf. Accessed February 2017," ESPC and Towngas International Company, 2007.
35. J. Simmons, "Study of Compressed Air Energy Storage with Grid and Photovoltaic Energy Generation," The Arizona Research Institute for Solar Energy (AzRISE) - APS Final Draft Report., University of Arizona, 2010.

## 162 Flywheels
Technology |  |  | Flywheels
year |  | 2018 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical | Mechanical
| Application | System | System | System | System | System | System | System | System
| Energy storage capacity for one unit [MWh] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | A, F, M
| Output capacity for one unit [MW] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | A, F, M
| Input capacity for one unit [MW] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.5 | A, F, M
| Round trip efficiency [%] | 98 | 98 | 98 | 98 | 98 | 99 | 98 | 99 | G, M
| - Charge efficiency [%] | 99 | 99 | 99 | 99 | 99 | 99.5 | 99 | 99.5 | G, M
| - Discharge efficiency [%] | 99 | 99 | 99 | 99 | 99 | 99.5 | 99 | 99.5 | G, M
| Energy losses during storage [%/day] | 5 | 3 | 1 | 1 | 2 | 5 | 0.5 | 1.5 | H | [16]
| Auxiliary electricity consumption [% of output] | ctrl: 0; -: C
| Forced outage [%] | ctrl: 0; -: [17]
| Planned outage [weeks/year] | ctrl: 0
| Technical lifetime [years] | 20 | 20 | 25 | 25 | 20 | 25 | 20 | 25 | B, M | [17]
| Construction time [years] | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | A, M
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | D, M
| Response time from full-rated charge to full-rated discharge [sec] | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | D, M
Financial data
| Specific investment [M€/MWh] | 1.0634 | 0.35624 | 0.35624 | 0.35624 | 0.31902 | 0.38282 | 0.31902 | 0.38282 | E, J, L | [18]
| - energy component [M€/MWh] | 1.0634 | 0.35092 | 0.35092 | 0.35092 | 0.31902 | 0.38282 | 0.31902 | 0.38282 | D
| - capacity component [M€/MW] | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.10634 | 0.095706 | 0.10634 | D
| Fixed O&M [€/MW/year] | 797.55 | 797.55 | 797.55 | 797.55 | 797.55 | 797.55 | 797.55 | 797.55 | D, M
| Variable O&M [€/MWh] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | I | [7]
Technology-specific data
| Specific investment [M€/MW] | 0.1744 | 0.15419 | 0.14462 | 0.13931 | 0.14888 | 0.15951 | 0.13824 | 0.14888 | A | [18]
| Specific energy [Wh/kg] | 115 | 350 | 350 | 350 | 300 | 400 | 350 | 400 | A
| Specific energy [Wh/l] | 500 | 1500 | 1500 | 1500 | 1300 | 2000 | 1300 | 2000 | A
| Cycle life | 106 | 106 | 106 | 106 | 106 | 107 | 106 | 107 | A
Notes:
A. Data informed by WattsUp Power February 2018
B. +25 years on mechanics. 15 years on electronics. Informed by WattsUp Power March 2017
C. 150 W during upstart procedure for 7 min informed by WattsUp Power. After upstart auxiliary power is included in round trip efficiency
D. Informed by WattsUp Power February 2018
E. Confer also Table 2
F. Please note that the mentioned 1 MW is standard size of one unit that can be assembled to larger entities functioning as “larger units” (somewhat similar to the case of cells in batteries). The displayed financial data is for a 2 MW plant. Flywheels can be connected and provide 20 MW regulation power and several MWh of storage capacity (this size is in commercial operation cf. Figure 5 above). Higher capacities can be obtained and the price/unit decreases when several units are purchased.
G. Informed by WattsUp Power February 2018
H. Loss/day measured by WattsUp Power. The projected losses towards 2050 is justified by results already now obtained by NASA
I. The variable costs of flywheels are not directly related to the power put in and out. The data is based on storing (and discharging) 33 MWh/day in 350 days/year. Data from WattsUp Power.
J. Displayed price information is based on recent WattsUp Power sales prices for two units (each 1 MW, 100 kWh). Price for one unit of 1 MW and 100 kWh is approx. 0.1 mill EUR. If several units are purchased unit price may be lower than by purchase of two units.
K. Based on plans for increasing rotational speed by a factor 3 (WattsUp Power)
L. The non-flywheel costs depend on the use of the flywheel. Demanding use patterns may increase non-flywheel costs from the 5 k€ (as included here) to 75 k€/MWh
M. Future uncertainties based on author´s best assessment
References:
[1] "http://www.elp.com/articles/2016/01/amber-kinetics-signs-flywheel-energy-storage-contract-with-pg-e.html," 2016. [Online]. [Accessed March 2017].
[2] e. a. I. Gyuk, "Grid Energy Storage," US Department of Energy, 2013.
[3] S.-i. Inage, "Prospects of Electricity Storage in Decarbonised Power Grids, IEA Working Paper Series," OECD/IEA, 2009.
[4] "Toshiba Leading Innovation," Toshiba. [Online]. [Accessed March 2017].
[5] "Fact sheet. Frequency Regulation and Flywheels," Beacon Power, 2010. Archived March 2017. Available on https://web.archive.org/web/20100331042630/http://www.beaconpower.com/files/Flywheel_FR-Fact-Sheet.pdf.
[6] "http://beaconpower.com," Beacon Power. [Online]. [Accessed March 2017].
[7] B. Z. a. S. Syri, "Electrical Energy Storage Systems: A comparative life cycle cost analysis," Renewable and Sustainable Energy Reviews, vol. 42, pp. 569-596, 2015.
[8] I. P. ,. E. S. Gyuk, "EPRI-DOE Handbook of Energy Storage for Transmission & Distribution Applications 1001834," US Department of Energy, Washington, 2003.
[9] "timesunion," Times Union, 2011. [Online]. [Accessed March 2017].
[10] "Joint EASE/EERA recommendations for a European Energy Storage Technology Development Roadmap towards 2030," EASE and EERA, Brussels, 2013.
[11] "Technology Roadmap, Energy Storage," International Energy Agency, Paris, 2013.
[12] N. K. Kohli, "Short-Term backup power through flywheel energy storage system. Available on https://www.slideshare.net/Drnavinkumarkohli/ppt-fly-wheel-navin-kohli (Accessed March 2017)," 2012.
[13] S. o. A. E. I. SAE, "https://global.ihs.com/doc_detail.cfm?rid=GS&&item_s_key=00138611," IHS Markit, 2013. [Online]. [Accessed March 2017].
[14] "Electrical Energy Storage," International Electrotechnical Commission, Geneva, Switzerland, 2011.
[15] 2. Private communication with WattsUp Power.
[16] W. Torell, "Lifecycle C arbon Footprint Analysis of Batteries vs. Flywheels, White Paper 209," Schneider Electric, 2015.
[17] W. V. H. Susan M. Schoenung, "Long- vs. Short-Term Energy Storage Technologies Analysis. A Life-Cycle Cost Study," Sandia National Laboratories, Albuquerque, New Mexico 87185 and Livermore, California 94550, 2003.
[18] "Lazard´s levelized cost of storage - Version 2.0," Lazard, 2016.
[19] e. a. P. Tayler, "Pathways for Energy Storage in the UK, Report 007," The Centre for Low Carbon Futures, March 2012.
[20] "https://www.calnetix.com/resource/flywheels/advantages-flywheels," Calnetix. [Online]. [Accessed March 2017].
[21] "http://www.climatetechwiki.org/technology/jiqweb-es-fw," [Online].
[22] P. N. N. L. Daryl Brown, "Federal Technology Alert. DOE/EE-0286," Federal Energy Management Program, 2003.
[23] "InflationData.com," InflationData, 2017. [Online]. [Accessed 2017].
[24] "Materials Roadmap Enabling Low Carbon Energy Technologies, Commission Staff Working Paper," European Commission, Brussels, 2011.
[25] "energy.gov," 2010. [Online]. [Accessed March 2017].
[26] "Scientific American," Scientific American, 2011. [Online]. [Accessed March 2017].
[27] e. a. M. Hedlund, "Flywheel Energy Storage for Automotive Applications," Energies, vol. 8, pp. 10636-10663, 2015.
[28] 2009. [Online]. [Accessed March 2017].
[29] Memoori, Smart Building Resesearch, 2017. [Online]. [Accessed MArch 2017].

## 180 Lithium Ion Battery
Technology |  | Lithium-ion NMC battery (Utility-scale, Samsung SDI E3-R135)
year |  | 2015 | 2020 | 2030 | 2040 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Application | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive
| Energy storage capacity for one unit [MWh] | 3.2 | 6 | 7 | 8 | 8 | 5 | 9 | 7 | 12 | A | [2,14]
| Output capacity for one unit [MW] | 9.6 | 18 | 21 | 24 | 24 | 16 | 21 | 22 | 28 | A,B | [2,14]
| Input capacity for one unit [MW] | 1.6 | 3 | 3.5 | 4 | 4 | 2.7 | 3.5 | 3.7 | 4.7 | A,B | [2,14]
| Round trip efficiency [%] AC | 91 | 91 | 92 | 92 | 92 | 90 | 92 | 91 | 94 | C | [3,21,22,51]
| Round trip efficiency [%] DC | 95 | 95 | 96 | 96 | 96 | 95 | 96 | 95 | 97 | C | [3,21,22,51]
| - Charge efficiency [%] | 98 | 98 | 98.5 | 98.5 | 98.5 | 98 | 98.5 | 98 | 99 | D | [2]
| - Discharge efficiency [%] | q | 97 | 97.5 | 97.5 | 97.5 | 97 | 98 | 97 | 98 | D | [2]
| Energy losses during storage [%/day] | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.2 | 0.05 | 0.15 | E | [18,50,52]
| Forced outage [%] | 0.4 | 0.38 | 0.35 | 0.3 | 0.25 | 0.2 | 0.5 | 0.1 | 0.3 | F
| Planned outage [weeks/year] | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.05 | 0.2 | F
| Technical lifetime [years] | 15 | 20 | 25 | 30 | 30 | 15 | 25 | 20 | 45 | G | [3,5,8,14]
| Construction time [years] | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.1 | 0.25 |  | [38]
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0 | 0.08 | H | [53]
| Response time from full-rated charge to full-rated discharge [sec] | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0 | 0.08 | 0 | 0.08 | H | [53]
Financial data
| Specific investment [M€/MWh] | 1.3697 | 1.1081 | 0.66143 | 0.41898 | 0.27117 | 0.93579 | 1.945 | 0.17652 | 1.0368 | I | [44,48]
| - energy component [M€/MWh] | 0.32753 | 0.14037 | 0.065931 | 0.04679 | 0.037219 | 0.074438 | 0.20098 | 0.027648 | 0.12229 | J | [44]
| - capacity component [M€/MW] PCS | 0.30839 | 0.28712 | 0.17014 | 0.10634 | 0.063804 | 0.25522 | 0.54233 | 0.042536 | 0.26585 | K | [54–56]
| - other project costs [M€/MWh] | 0.11697 | 0.10634 | 0.085072 | 0.05317 | 0.042536 | 0.095706 | 0.11697 | 0.021268 | 0.11697 | L | [22,40,54]
| Fixed O&M [k€/MW/year] | 0.57424 | 0.57424 | 0.57424 | 0.57424 | 0.57424 | 0.47853 | 0.57424 | 0.42536 | 0.57424 | M | [22]
| Variable O&M [€/MWh] | 2.2331 | 2.1268 | 1.9141 | 1.8078 | 1.7014 | 0.42536 | 5.955 | 0.31902 | 2.6585 | N | [55]
Technology-specific data
| Energy storage expansion cost [M€/MWh] | 0.4445 | 0.24671 | 0.151 | 0.09996 | 0.079755 | 0.17014 | 0.27542 | 0.048916 | 0.18716 | O | [44,48]
| Output capacity expansion cost [M€/MW] | 0.30839 | 0.28712 | 0.17014 | 0.10634 | 0.063804 | 0.25522 | 0.54233 | 0.042536 | 0.26585 | P | [54–56]
| Alternative Investment cost [M€/MW] | 0.41473 | 0.35092 | 0.21268 | 0.12761 | 0.085072 | 0.29775 | 0.61677 | 0.05317 | 0.32965 | Q | [41,44,48,54–56]
| Lifetime in total number of cycles | 6000 | 14000 | 30000 | 40000 | 50000 | 10000 | 16000 | 20000 | 70000 | R | [3–5,14]
| Specific power [W/kg] | 285 | 315 | 417 | 522 | 627 | 300 | 420 | 450 | 900 | S | [2,24]
| Power density [kW/m3] | 354 | 390 | 519 | 648 | 780 | 450 | 600 | 600 | 1200 | S | [2,24]
| Specific energy [Wh/kg] | 95 | 105 | 139 | 174 | 209 | 100 | 140 | 150 | 300 | S | [2,24]
| Energy density [kWh/m3] | 118 | 130 | 173 | 216 | 260 | 150 | 200 | 200 | 400 | S | [2,24]
Notes
A. One unit defined as a 40 feet container including LIB system and excluding power conversion system. Values for 2020-2030 are taken from Samsung SDI brochures for grid-connected LIBs from 2016 and 2018 [2,14]. This unit of 3.2MWh/9.6MW (3C) is a typical size grid scale battery. The Specific investment cost under financial data is provided for a 1MWh : 3MW (3C) battery. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
B. Power input/output are set to 0.5/3 times the energy capacity as it is the standard grid-connected LIBs designed for power purposes [2,14]. It is noted that the power capacity is strongly dependent on the battery type and chemistry.
C. The gradual change towards lower C-rates following the transition from frequency regulation to renewable integration promotes lower C-rates. Therefore the average DC roundtrip efficiency is expected to increase slightly. The RT eff. vs. C-rate is exemplified in Figure 7 [3,51]. The AC roundtrip efficiency includes losses in the power electronics and is 2-4% lower than the DC roundtrip efficiency. The total roundtrip efficiency further includes standby losses making the total roundtrip efficiency typically ranging between 80% and 90% [21,22].
D. The C-rate is 0.5 during charge and up to 6 during discharge for the Samsung SDI batteries [2,14]. The presented conversion efficiencies assume average discharge C-rates in 2020-2020 around 3 and charge C-rates around 0.5.
E. Lithium-ion battery daily discharge loss. The central estimates for self-discharge of Li-ion batteries range between 0.05% and 0.20% a day in 2016 and are expected to stay flat to 2030.
F. It is expected not to have any outage during lifetime of the grid-connected LIB. Only a few days during the e.g. 15 years life time is needed for service and exchanging fans and blowers for thermal management system and power conversion system. Forced outage is expected to drop with increasing robustness following the learning rate and cumulated production. Planned outage is expected to decrease after 2020 due to increased automation.
G. Current state-of-the-art NMC LIB has 20 years lifetime. The NMC lifetime is expected to reach LTO lifetime by 2020 and 30 years lifetime for grid-connected LIBs in 2040 and 2050 as photovoltaic power systems have today [3,5,8,14].
H. The response time is obtained from simulated response time experiments with hardware in the loop [53].
I. The system specific forecasts includes rack, TMS, BMS, EMS and PCS (Figure 5). The forecast is calculated as the sum of the PCS, the battery cell, and other costs. The system specific forecast is exclusive power cables to the site and entrepreneur work for installation of the containers [44,48]. The specific investment cost is the total cost of a 1MWh : 3MW (3C) battery, which is the typical grid scale battery defined in note A. Cost examples of a 2MWh/8MW and a 16MWh/4MW battery are given in the section below.
J. The battery pack cost forecast is provided in Figure 8 and the related text [44].
K. Power conversion cost is strongly dependent on scalability and application. The PCS cost is based on references [54–56] and reflects the necessity for high power performance and compliance to grid codes to provide ancillary services, bidirectional electricity flow and two-stage conversion, as well as the early stage of development and the fact that few manufacturers can guarantee turnkey systems. Inverter replacement is expected every 10 years. The bidirectional inverter given here has more or less the same charge and discharge capacity (MW).
L. Other costs include construction costs and entrepreneur work. These costs heavily dependent on location, substrate and site access. Power cables to the site and entrepreneur work for installation of the containers are included in other costs. Therefore other costs are assumed to – roughly – correlate with the system size. Automation is expected to decrease other costs from 2030 and onwards. Estimates are aggregated from the literature [22,40,54].
M. Fixed O&M is assumed to be constant, although the O&M may depend on the application [22].
N. Variable O&M is assumed to be 2.1 EUR/MWh in 2020 with a range of 0.4 – 5.6 [55].
O. Since multi-MWh LIB systems are scalar, the energy storage expansion cost is here estimated to be equal to the energy component plus the “other costs” [44,48].
P. Since multi-MW LIB systems are scalar, the capacity expansion cost equals the capacity component cost [54–56].
Q. The alternative investment cost in M€2020/MW is specified for a 4C, 0.25 h system as for the Laurel Mountain, West Virginia, USA grid-scale LIB storage system [41]. I.e. the alternative investment cost is 25% of the energy storage expansion cost plus the PCS cost [41,44,48,54–56].
R. Cycle life specified as the number of cycles at 1C/1C to 80% state-of-health. Samsung SDI 2016 whitepaper on ESS solutions provide 15 year lifetime for current modules operating at C/2 to 3C [14]. Steady improvement in battery lifetime due to better materials and battery management is expected. Kokam ESS solutions are also rated at more than 8000-20000 cycles (80-90% DOD) based on chemistry [3]. Thus for daily full charge-discharge cycles, the batteries are designed to last for 15-50 years if supporting units are well functioning. Lifetimes are given for both graphite and LTO anode based commercial batteries from Kokam. Cycle lives are steadily increasing over last few years as reflected in 2020/2030 numbers [4,5,14].
S. Specific power, power density, Specific energy and energy density is provided for discharge mode, starting with the values provided in the section “Typical characteristics and capacities”. A charge/discharge conversion factor of 12 can be derived from this section. For this datasheet, a discharge rate of 3C is assumed. The expected development depends on the successive R&D progress as indicated in the section “Research and development perspectives” [2,24].
References
[1] Leclanche. Lithium Ion Technology and Product Description, (2018). http://www.leclanche.com/technology-products/leclanche-technology/lithium-ion-cells/
[2] Samsung. ESS Batteries by Samsung SDI Top Safety & Reliability Solutions, (2018). http://www.samsungsdi.com/upload/ess_brochure/201809_SamsungSDI ESS_EN.pdf
[3] L. Kokam Co. Total Energy Storage Solution Provider, (2018). http://kokam.com/data/2018_Kokam_ESS_Brochure_ver_5.0.pdf
[4] L. Kokam Co. Kokam Li-ion/Polymer Cell, (2017). http://kokam.com/data/Kokam_Cell_Brochure_V.4.pdf
[5] StoraXe. StoraXe Industrial & Infrastructure Scalable battery storage system, (2018). https://www.ads-tec.de/fileadmin/download/doc/brochure/Datasheet_Energy_Industrial_EN.pdf
[6] Fronius. Fronius Energy Package, (2018). http://www.fronius.com/en/photovoltaics/products/all-products/solutions/fronius-storage-solution/fronius-energy-package/fronius-energy-package
[7] Fenecon. Fenecon Commercial 50-series Battery Module ¦ Battery Rack, (2018). https://www.fenecon.de/en_US/page/infocenter#fenecon-industrial
[8] Altairnano. 24 V 60 Ah Battery Module, (2016). https://altairnano.com/products/battery-module/
[9] S. Weintraub, Electrek. Tesla Gigafactory tour roundup and tidbits: ‘This is the coolest factory in the world’, (2016). https://electrek.co/2016/07/28/tesla-gigafactory-tour-roundup-and-tidbits-this-is-the-coolest-factory-ever/
[10] M. Kane, InsideEVs. BMW i3 Samsung SDI 94 Ah Battery Rated For 524,000 Miles, (2018). https://insideevs.com/lets-look-at-the-specs-of-the-samsung-sdi-94-ah-battery/
[11] Qnovo. Inside the Battery of a Nissan Leaf, (2018). https://qnovo.com/inside-the-battery-of-a-nissan-leaf/
[12] J.M. Tarascon, M. Armand. Issues and challenges facing rechargeable lithium batteries, Nature, 414 (2001) 359. doi:10.1038/35104644
[13] Shutterstock. Tesla 2170 battery cell stock photos, (2018). https://www.shutterstock.com/search/tesla+2170+battery+cell
[14] Samsung, Smart Battery Systems for Energy Storage, (2016). http://www.samsungsdi.com/upload/ess_brochure/Samsung SDI brochure_EN.pdf
[15] Inside EVs. LCChem Prismatic Cell, (2018). https://insideevs.com/wp-content/uploads/2015/12/ess_cell1.jpg
[16] H.C. Hesse, M. Schimpe, D. Kucevic, A. Jossen. Lithium-ion battery storage for the grid - A review of stationary battery storage system design tailored for applications in modern power grids, Energies, 10 (2017) 2107. doi:10.3390/en10122107
[17] M. Schimpe, M. Naumann, N. Truong, H.C. Hesse, S. Santhanagopalan, A. Saxon, A. Jossen. Energy efficiency evaluation of a stationary lithium-ion battery container storage system via electro-thermal modeling and detailed component analysis, Appl. Energy. 210 (2018) 211. doi:10.1016/j.apenenergy.2017.10.129
[18] Electropaedia. Battery Performance Characteristics - How to specify and test a battery, (2018). https://www.mpoweruk.com/performance.htm
[19] L. Kokam Co. Lithium Ion Polymer Cells - High Energy High PowerㅣKokam Battery Cells, (2018). http://kokam.com/cell/
[20] Sempra Renewables. Auwahi Wind, (2012). http://www.semprarenewables.com/project/auwahi-wind/
[21] A.H. Fathima, K. Palanisamy. Renewable systems and energy storages for hybrid systems, Ed(s): A. Hina Fathima, et al., in Hybrid-renewable energy systems in microgrids. Woodhead Publishing (2018), pp. 162. https://doi.org/10.1016/B978-0-08-102493-5.00008-X
[22] Lazard. Levelized Cost of Storage (2017)., https://www.lazard.com/perspective/levelized-cost-of-storage-2017/
[23] R. Hidalgo-León et al. A survey of battery energy storage system (BESS), applications and environmental impacts in power systems, 2017 IEEE 2nd ETCM pp. 1–6. doi:10.1109/etcm.2017.8247485.
[24] LG Chem. Change your energy. Change your life., (2018). http://www.lgchem.com/upload/file/product/LGChem_Catalog_Global_2018.pdf
[25] Researchinterfaces. Lithium-ion batteries for large-scale grid energy storage, (2018). https://researchinterfaces.com/lithium-ion-batteries-grid-energy-storage/
[26] U.S. EPA. Application of Life-Cycle Assessment to Nanoscale Technology: Lithium-ion Batteries for Electric Vehicles, United States Environ. Prot. Agency. (2013) 1–119. doi:10.1038/nchem.2085.
[27] J.F. Peters, M. Baumann, B. Zimmermann, J. Braun, M. Weil. The environmental impact of Li-Ion batteries and the role of key parameters – A review, Renew. Sustain. Energy Rev. 67 (2017) 491–506. doi:10.1016/j.rser.2016.08.039
[28] The Washington Post. The environmental impact of cobalt mining, (2018). https://www.washingtonpost.com/news/in-sight/wp/2018/02/28/the-cost-of-cobalt/?utm_term=.eebc6c00f0de
[29] Visualcapitalist. Nickel: The Secret Driver of the Battery Revolution, (2017). http://www.visualcapitalist.com/nickel-secret-driver-battery-revolution/
[30] Bloomberg. We’re Going to Need More Lithium, (2017). https://www.bloomberg.com/graphics/2017-lithium-battery-future/
[31] R. Petibon, J. Xia, L. Ma, M.K.G. Bauer, K.J. Nelson, J.R. Dahn. Electrolyte System for High Voltage Li-Ion Cells, J. Electrochem. Soc. 163 (2016) A2571–A2578. doi:10.1149/2.0321613jes
[32] A. Casimir, H. Zhang, O. Ogoke, J.C. Amine, J. Lu, G. Wu. Silicon-based anodes for lithium-ion batteries: Effectiveness of materials synthesis and electrode preparation, Nano Energy. 27 (2016) 359–376. doi:10.1016/j.nanoen.2016.07.023
[33] M. Saulnier, A. Auclair, G. Liang, S.B. Schougaard. Manganese dissolution in lithium-ion positive electrode materials, Solid State Ionics. 294 (2016) 1–5. doi:10.1016/j.ssi.2016.06.007
[34] E.-Y. Kim, B.-R. Lee, G. Yun, E.-S. Oh, H. Lee. Effects of binder content on manganese dissolution and electrochemical performances of spinel lithium manganese oxide cathodes for lithium ion batteries, Curr. Appl. Phys. 15 (2015) 429–434. doi:10.1016/j.cap.2015.01.029
[35] S. Lee, E.-Y. Kim, H. Lee, E.-S. Oh. Effects of polymeric binders on electrochemical performances of spinel lithium manganese oxide cathodes in lithium ion batteries, J. Power Sources. 269 (2014) 418–423. doi:10.1016/j.jpowsour.2014.06.167
[36] eeNews Power Management. Revolutionary solid state rechargeable aluminium-sulfur battery project starts, (2017). http://www.eenewspower.com/news/revolutionary-solid-state-rechargeable-aluminium-sulfur-battery-project-starts
[37] Ørsted. Ørsted takes first steps into commercial energy storage, (2018). https://orsted.com/en/Media/Newsroom/News/2018/04/Orsted-takes-first-steps-into-commercial-battery-storage
[38] Tesla. Addressing Peak Energy Demand with the Tesla Powerpack, (2016). https://www.tesla.com/da_DK/blog/addressing-peak-energy-demand-tesla-powerpack?redirect=no
[39] Electrek. Tesla quietly brings online its massive - biggest in the world - 80 MWh Powerpack station with Southern California Edison, (2017). https://electrek.co/2017/01/23/tesla-mira-loma-powerpack-station-southern-california-edison/
[40] Tesla. Tesla Powerpack to Enable Large Scale Sustainable Energy to South Australia, (2017). https://www.tesla.com/da_DK/blog/Tesla-powerpack-enable-large-scale-sustainable-energy-south-australia?redirect=no Page
[41] Energy Storage Association. Frequency Regulation Services and a Firm Wind Product: AES Energy Storage Laurel Mountain Battery Energy Storage, (2018). http://energystorage.org/energy-storage/case-studies/frequency-regulation-services-and-firm-wind-product-aes-energy-storage
[42] ABB. Battery energy storage system PQpluS, (2018). https://new.abb.com/high-voltage/capacitors/lv/bess-products/PQpluS
[43] S. Saylors, Philip C. Kjær. Rasmus Lærke. Ancillary Services Provided from Wind Power Plant Augmented with Energy Storage, (2014). https://www.ieee-pes.org/presentations/gm2014/PESGM2014P-000718.pdf
[44] Bloomberg New Energy Finance. New Energy Outlook 2018, (2018). https://bnef.turtl.co/story/neo2018.pdf?autoprint=true&teaser=true
[45] CleanTechnica. $100/kWh Tesla Battery Cells This Year, $100/kWh Tesla Battery Packs In 2020¦, (2018). https://cleantechnica.com/2018/06/09/100-kwh-tesla-battery-cells-this-year-100-kwh-tesla-battery-packs-in-2020/
[46] Wardsauto. Two Tidbits From CES: Better Cybersecurity and Cheaper EV Batteries, (2017). https://www.wardsauto.com/ideaxchange/two-tidbits-ces
[47] Visualcapitalist. China Leading the Charge for Lithium-Ion Megafactories, (2017) http://www.visualcapitalist.com/china-leading-charge-lithium-ion-megafactories/
[48] International Renewable Energy Agency. IRENA Battery Storage Report, (2015). http://www.irena.org/-/media/Files/IRENA/Agency/Publication/2015/IRENA_Battery_Storage_report_2015.pdf
[49] Windpower Engineering & Development. Global battery energy-storage system installed capacity will exceed 14 GW by 2020, (2016). https://www.windpowerengineering.com/business-news-projects/global-battery-energy-storage-system-installed-capacity-will-exceed-14-gw-2020/
[50] International Renewable Energy Agency. Electricity Storage and Renewables : Costs and Markets To 2030, (2017). http://www.irena.org/publications/2017/Oct/Electricity-storage-and-renewables-costs-and-markets
[51] Danish Technological Institute. BESS project Smart grid ready Battery Energy Storage System for future grid, (2017). https://www.energiforskning.dk/sites/energiteknologi.dk/files/slutrapporter/bess_final_report_forskel_10731.pdf
[52] H. Chen, T.N. Cong, W. Yang, C. Tan, Y. Li, Y. Ding, Progress in electrical energy storage system: A critical review, Prog. Nat. Sci. 19 (2009) 291–312. doi:10.1016/j.pnsc.2008.07.014
[53] D.M. Greenwood, K.Y. Lim, C. Patsios, P.F. Lyons, Y.S. Lim, P.C. Taylor, Frequency response services designed for energy storage, Appl. Energy. 203 (2017) 115–127. doi:10.1016/j.apenergy.2017.06.046
[54] R. Benato, G. Bruno, F. Palone, R.M. Polito, M. Rebolini, Large-scale electrochemical energy storage in high voltage grids: Overview of the Italian experience, Energies. 10 (2017) 1-17. doi:10.3390/en10010108
[55] B. Zakeri, S. Syri, Electrical energy storage systems: A comparative life cycle cost analysis, Renew. Sustain. Energy Rev. 42 (2015) 569–596. doi:10.1016/j.rser.2014.10.011
[56] G. Huff, A.B. Currier, B.C. Kaun, D.M. Rastler, S.B. Chen, D.T. Bradshaw, W.D. Gauntlett, DOE/EPRI electricity storage handbook in collaboration with NRECA, (2015). https://www.sandia.gov/ess-ssl/publications/SAND2015-1002.pdf

## 181 Vanadium Redox Flow Battery
Technology |  | Vanadium Redox Battery (VRB)
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Application | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive
| Energy storage capacity for one unit [MWh] | 2 | 2 | 2 | 2 | 0.4 | 800 | 0.4 | 800 | A,M | [4]+[9]
| Output capacity for one unit [MW] | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 200 | 0.1 | 200 | A,M | [4]
| Input capacity for one unit [MW] | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 200 | 0.1 | 200 | A,M | [4]
| Round trip efficiency DC [%] | 78 | 78 | 78 | 78 | 62 | 88 | 67 | 95 | B | [5];[22]
- Charge efficiency [%] | bar: ctrl to Upper
- Discharge efficiency [%] | bar: ctrl to Upper
| Energy losses during storage [%/day] | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | C | [4];[22]
| Forced outage [%] | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 5 | 0 | 5 | D,M | [1]
| Planned outage [weeks/year] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | D,M | [1]
| Technical lifetime [years] | 20 | 20 | 20 | 20 | 6 | 23 | 8 | 32 |  | [4];[28]+[22]
| Construction time [years] | 1 | 1 | 1 | 1 | 0.2 | 2 | 0.2 | 2 | E,M | [9]
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.1 | 0.1 | 0.1 | 0.1 | 0.005 | 2 | 0.005 | 2 | F,G | [4]+[30]
| Response time from full-rated charge to full-rated discharge [sec] | 0.07 | 0.07 | 0.07 | 0.07 | 0.004 | 1.4 | 0.004 | 1.4 | F,G,M | [1]
Financial data
| Specific investment [M€/MWh] | 0.79755 | 0.63804 | 0.37219 | 0.35092 | 0.5636 | 1.2229 | 0.31902 | 0.61677 | H | [22]+[27]/[19]
| - energy component [M€/MWh] | 0.61677 | 0.47853 | 0.25522 | 0.23395 | 0.40409 | 0.9996 | 0.20205 | 0.4679 | H, I | [22]+[27]
| - capacity component [M€/MW] | 0.47853 | 0.43599 | 0.35092 | 0.35092 | 0.45726 | 0.51043 | 0.37219 | 0.41473 | H | [22]+[25]+[27]/[19]
| - other project costs [M€/MWh] | 0.063804 | 0.05317 | 0.031902 | 0.031902 | 0.042536 | 0.095706 | 0.021268 | 0.05317 | J | [19]
| Fixed O&M [% total investment] | 2 | 2 | 1.5 | 1.5 | 0.8 | 4.1 | 0.6 | 3.1 |  | [24]+[25]/[2]
| Variable O&M [€/MWh] | 0.95706 | 0.95706 | 0.95706 | 0.95706 | 0.21268 | 2.9775 | 0.21268 | 2.9775 | 0 | [25]/[2]
Technology-specific data
| Alternative Investment cost [M€/MW] | 3.1902 | 2.5522 | 1.4888 | 1.3824 | 2.2331 | 4.8916 | 1.2761 | 2.4458 | H | [22]+[31]+[27]/[19]
| Lifetime in total number of cycles | -¦- | -¦- | -¦- | -¦- | -¦- | -¦- | -¦- | -¦- | K | [1]
| Specific power [W/kg] | 2.9 | 2.9 | 2.9 | 2.9 | 1.45 | 3.63 | 1.45 | 3.63 | A,L,M | [4]
| Power density [W/m3] | 2260 | 2260 | 2260 | 2260 | 1130 | 2825 | 1130 | 2825 | A,L,M | [4]
| Specific energy [Wh/kg] | 11.8 | 11.8 | 11.8 | 11.8 | 5.9 | 14.75 | 5.9 | 14.75 | A,L,M | [4]
| Energy density [Wh/m3] | 9040 | 9040 | 9040 | 9040 | 4520 | 11300 | 4520 | 11300 | A,L,M | [4]
Notes:
A. One Uni.System unit from UniEnergy Technologies. Installation sizes vary from tens of kW to hundreds of MW.
B. Efficiency varies depending on use.
C. Energy losses depend on idle situation. If pumps are off and electrolyte not present in the reaction stack no energy loss occurs. This increases response time (see above). Self-discharge only occurs for electrolyte inside the reaction stack. This is a relatively small volume and the self-discharge will be at most 2 % over time for typical installations. Losses related to stand-by energy consumption of pumps are not included.
D. Some companies guarantee at least 99.5% uptime.
E. Depends highly on the installation.
Time is less than 100 ms for idle situation with electrolyte in reaction stack and pumps on [4]. Less the 1 s if electrolyte must first be pumped [5]. Less than 1 min if pumps are not on [5]. PCS might be limiting the response time.
G. Might in practice be limited by PCS.
H. Valid for installations with rated discharge times of 4 hours. Use equation in “Prediction of performance and cost” above to calculate for installations with a different rated discharge time.
I. Composed of both electrolyte etc. at 347 EUR/kWh and stack at 1313 EUR/kW [22].
J. Value for utility T&D installations with discharge time of 4 hours used.
K. Manufactures state unlimited number of cycles during technical lifetime [4], [5].
L. Varies with capacity to storage ratio. Is significantly lower for some manufactures.
M. Uncertainties are based on a qualified guess.
References
[1] M. Manahan, N. Jewell, D. Link, and B. Westlake, “Program on Technology Innovation: Assessment of Flow Battery Technologies for Stationary Applications,” EPRI, 2016.
[2] M. Guarnieri, P. Mattavelli, G. Petrone, and G. Spagnuolo, “Vanadium Redox Flow Batteries: Potentials and Challenges of an Emerging Storage Technology,” IEEE Ind. Electron. Mag., vol. 10, no. 4, pp. 20–31, 2016.
[3] M. Skyllas-Kazacos, “SECONDARY BATTERIES – FLOW SYSTEMS ¦ Vanadium Redox-Flow Batteries,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 444–453.
[4] UniEnergy Technologies, “Uni.System product data,” 2016.
[5] Vionx Energy, “VNX 1000 SERIES Product data,” 2017.
[6] UniEnergy Technologies, Product material: Maximizing Value Thorugh UET Energy Storage. 2015.
[7] Z. Yang et al., “Electrochemical Energy Storage for Green Grid,” Chem. Rev., vol. 111, no. 5, pp. 3577–3613, May 2011.
[8] Sumitomo Electric Group, REDOX FLOW BATTERY: Product material. 2016.
[9] “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
[10] Sumitomo Electric Group, “Container Type Redox Flow Battery System,” 2017.
[11] IEC, “Electrical Energy Storage,” 2011.
[12] “Sumitomo Electric Industries, Ltd. ¦ Press Release (2013) Selected to be Subsidized by the Governmental Program for Urgent Demonstration Project of Large-scale Energy Storage Systems.” [Online]. Available: http://global-sei.com/news/press/13/prs088_s.html. [Accessed: 30-Mar-2017].
[13] J. Cho, S. Jeong, and Y. Kim, “Commercial and research battery technologies for electrical energy storage applications,” Prog. Energy Combust. Sci., vol. 48, pp. 84–101, Jun. 2015.
[14] T. Biesheuvel and M. Burton, “It’s Boom Time for Vanadium, Ruthenium and Cobalt - Bloomberg,” Bloomberg Markets, 2017. [Online]. Available: https://www.bloomberg.com/news/articles/2017-08-23/obscure-metal-used-to-fight-crusaders-has-surged-67-in-a-month. [Accessed: 06-Dec-2017].
[15] C. K. Charlotte Radford, Anna Xu, “GLOBAL VANADIUM WRAP: Prices rise across the board amid tight supply of V2O5 ¦ Metal Bulletin.com,” 2017. [Online]. Available: https://www.metalbulletin.com/Article/3768052/GLOBAL-VANADIUM-WRAP-Prices-rise-across-the-board-amid-tight-supply-of-V2O5.html. [Accessed: 18-Dec-2017].
[16] M. Moore, R. Counce, J. Watson, and T. Zawodzinski, “A Comparison of the Capital Costs of a Vanadium Redox-Flow Battery and a Regenerative Hydrogen-Vanadium Fuel Cell,” J. Adv. Chem. Eng., vol. 5, no. 4, pp. 5–7, 2015.
[17] M. C. S. U.S. Geological Survey, “VANADIUM (Data in metric tons of vanadium content unless otherwise noted),” 2014.
[18] O. Schmidt, A. Hawkes, A. Gambhir, and I. Staffell, “The future cost of electrical energy storage based on experience rates,” Nat. Energy, vol. 2, no. 8, p. 17110, Jul. 2017.
[19] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
[20] L. Baumann and E. Boggasch, “Experimental assessment of hydrogen systems and vanadium-redox-flow-batteries for increasing the self-consumption of photovoltaic energy in buildings,” Int. J. Hydrogen Energy, vol. 41, no. 2, pp. 740–751, 2016.
[21] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
[22] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
[23] G. Kear, A. A. Shah, and F. C. Walsh, “Development of the all-vanadium redox flow battery for energy storage: a review of technological, financial and policy aspects,” Int. J. Energy Res., vol. 36, no. 11, pp. 1105–1120, Sep. 2012.
[24] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
[25] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[26] M. Skyllas-Kazacos and J. F. McCann, “Chapter 10 – Vanadium redox flow batteries (VRBs) for medium- and large-scale energy storage,” in Advances in Batteries for Medium and Large-Scale Energy Storage, 2015, pp. 329–386.
[27] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
[28] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
[29] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
[30] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
[31] I. Renewable Energy Agency, “IRENA-IEA-ETSAP Technology Brief 5: Electricity Storage,” 2012.

## 182 Na-S Battery
Technology |  |  | NaS battery
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Application | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive | System, power- and energy-intensive
| Energy storage capacity for one unit [MWh] | 250 | 300 | 300 | 300 | 30 | 3000 | 30 | 3000 | A B,Q | [9]
| Output capacity for one unit [MW] | 35 | 50 | 50 | 50 | 5 | 500 | 5 | 500 | A,B,Q | [9]
| Input capacity for one unit [MW] | 35 | 50 | 50 | 50 | 5 | 500 | 5 | 500 | A,B,Q | [9]
| Round trip efficiency DC [%] | 83 | 83 | 85 | 85 | 71 | 92 | 74 | 96 | C | [9];[26]
- Charge efficiency [%] | bar: ctrl to Upper
- Discharge efficiency [%] | bar: ctrl to Upper
| Energy losses during storage [%/day] | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | D,Q | [11]/[30]/[26]
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | E,Q | [13]
| Planned outage [weeks/year] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F,Q | [13]
| Technical lifetime [years] | 15 | 19 | 24 | 24 | 10 | 28 | 14 | 36 | G | [13];[25]+[27]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 2 | 0.2 | 2 | Q | [1]
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.02 | 0.001 | 0.02 | H | [10]+[28]
| Response time from full-rated charge to full-rated discharge [sec] | 0.05 | 0.05 | 0.05 | 0.05 | 0.001 | 0.05 | 0.001 | 0.05 | H,I,Q | [9]
Financial data
| Specific investment [M€/MWh] | 0.48916 | 0.39346 | 0.24458 | 0.21268 | 0.26585 | 0.77628 | 0.13824 | 0.41473 | G | [22];[25]+[26]
| - energy component [M€/MWh] | 0.32965 | 0.26585 | 0.14888 | 0.11697 | 0.19141 | 0.5317 | 0.085072 | 0.24458 | G, J | [22]+[26]
| - capacity component [M€/MW] | 0.66994 | 0.43599 | 0.35092 | 0.35092 | 0.23395 | 0.82945 | 0.19141 | 0.68058 | G, K | [22]+[26]
| - other project costs [M€/MWh] | 0.063804 | 0.05317 | 0.031902 | 0.031902 | 0.042536 | 0.10634 | 0.021268 | 0.05317 | G | [22]+[26]
| Fixed O&M [% total investment] | 1.5 | 1.5 | 1.5 | 1.5 | 0.8 | 7.2 | 0.8 | 7.2 | G,L,M | [23];[24]
| Variable O&M [€/MWh] | 1.9141 | 1.9141 | 1.9141 | 1.9141 | 0.31902 | 5.955 | 0.31902 | 5.955 | G | [24]+[23]
Technology-specific data
| Alternative Investment cost [M€/MW] | 3.5092 | 2.3395 | 1.4888 | 1.2761 | 1.5951 | 4.679 | 0.85072 | 2.4458 | G | [22];[25]+[26]
| Lifetime in total number of cycles | 4500 | 5600 | 7500 | 7500 | 1100 | 11200 | 1500 | 15000 | N, G | [9];[25]+[27]
| Specific power [W/kg] | 9.3 | 9.3 | 9.3 | 9.3 | 6.98 | 11.63 | 6.98 | 11.63 | O,P,Q | [10]
| Power density [W/m3] | 4300 | 4300 | 4300 | 4.3 | 3225 | 5375 | 3225 | 5375 | O,P,Q | [10]
| Specific energy [Wh/kg] | 56 | 56 | 56 | 56 | 42 | 70 | 42 | 70 | O,P,Q | [10]
| Energy density [Wh/m3] | 26000 | 26000 | 26000 | 26000 | 19500 | 32500 | 19500 | 32500 | O,P,Q
Notes:
A. Specific Italian installation from 2015 used here as example. Assuming installations similar to Buzen City discussed above to become standard in the future.
B. Highly modular technology type with near linear scaling between total cost and installation size. Power and storage capacity cannot be varied independently.
C. Grid size unit including balancing and auxiliary losses. Excluding converters. Assumes no improvement between 2030 and 2050.
D. Ohmic losses maintain the temperature of the battery during operation. Losses are thus included in round trip efficiency [7]. No electrical self-discharge. If idle the heat loss is as much as 1 % of storage capacity/hour but highly variational. IRENA reports as “worst” value og 1.0 % [26]
E. Forced outage is minimal. Only reported case is a 2011 fire incident [9].
F. On the order of 1 h/year.
G. Assumptions for development and uncertainty discussed above in “Prediction of performance” and “Uncertainty”.
H. Due to absence of predictions in literature, no development is assumed as an estimate.
I. Measurement. Possibly limited by PCS.
J. Includes “Batteries” from reference [22] for 2015 values.
K. Includes “PCS-SCI”, “Auxiliary equipment”, and “Switching and actuating equipment” from reference [22] for 2015 values.
L. Highly uncertain. Reported in range 2000 to 17300 EUR2015/MW/year [24]
M. Does not include replacement costs. The batteries do not need replacement within lifetime [13],[10].
N. See Figure 5.
O. Data for standard NGK container unit.
P. Not the technological maximum values, i.e., the density of single cells, but the specifications for a full market-standard commercial product.
Q. Uncertainties are based on a qualified guess.
References:
[1] NGK Insulators LTD, “Case Studies.” pp. 1–13, 2016.
[2] “DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
[3] IEC, “Electrical Energy Storage,” 2011.
[4] C.-H. Dustmann and A. Bito, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS ¦ Safety,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 324–333.
[5] B. Dunn, H. Kamath, and J.-M. Tarascon, “Electrical Energy Storage for the Grid: A Battery of Choices,” Science (80-. )., vol. 334, no. 6058, pp. 928–935, 2011.
[6] J. Cho, S. Jeong, and Y. Kim, “Commercial and research battery technologies for electrical energy storage applications,” Prog. Energy Combust. Sci., vol. 48, pp. 84–101, Jun. 2015.
[7] J. Garche and C. K. Dyer, Encyclopedia of electrochemical power sources. Academic Press, 2009.
[8] R. Holze, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS: Sodium-Sulfur,” in Encyclopedia of Electrochemical Power Systems, vol. 200, 2009, pp. 302–311.
[9] M. Andriollo et al., “Energy intensive electrochemical storage in Italy: 34.8 MW sodium-sulphur secondary cells,” J. Energy Storage, vol. 5, pp. 146–155, Feb. 2016.
[10] NGK Insulators LTD, “Structure of NAS Energy Storage System,” 2016. [Online]. Available: https://www.ngk.co.jp/nas/specs/.
[11] H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.
[12] NGK Insulators LTD, “The World’s Largest NAS Battery Installation Commences Operation Short Installation Period Achieved through Containerized, Compact Format,” 2016. [Online]. Available: http://www.ngk.co.jp/english/news/2016/0303.html.
[13] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
[14] NGK Insulators LTD, “Comparison of Battery Technologies ¦ Why NAS? ¦ NAS.” [Online]. Available: https://www.ngk.co.jp/nas/why/comparison.html. [Accessed: 13-Sep-2017].
[15] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
[16] Z. Wen, Y. Hu, X. Wu, J. Han, and Z. Gu, “Main Challenges for High Performance NAS Battery: Materials and Interfaces,” Adv. Funct. Mater., vol. 23, no. 8, pp. 1005–1018, Feb. 2013.
[17] G. Kim, Y.-C. Park, Y. Lee, N. Cho, C.-S. Kim, and K. Jung, “The effect of cathode felt geometries on electrochemical characteristics of sodium sulfur (NaS) cells: Planar vs. tubular,” J. Power Sources, vol. 325, pp. 238–245, Sep. 2016.
[18] S. I. Kim, W. Il Park, K. Jung, and C.-S. Kim, “An innovative electronically-conducting matrix of the cathode for sodium sulfur battery,” J. Power Sources, vol. 320, pp. 37–42, Jul. 2016.
[19] K. . Ahlbrecht, C. Bucharsky, M. Holzapfel, J. Tübke, and M. J. Hoffmann, “Investigation of the wetting behavior of Na and Na alloys on uncoated and coated Na-β”-alumina at temperatures below 150 °C,” Ionics (Kiel)., pp. 1–9, Mar. 2017.
[20] X. Yu and A. Manthiram, “Ambient-Temperature Sodium-Sulfur Batteries with a Sodiated Nafion Membrane and a Carbon Nanofiber-Activated Carbon Composite Electrode,” Adv. Energy Mater., vol. 5, no. 12, pp. 1–6, 2015.
[21] X. Yu and A. Manthiram, “Performance Enhancement and Mechanistic Studies of Room-Temperature Sodium–Sulfur Batteries with a Carbon-Coated Functional Nafion Separator and a Na 2 S/Activated Carbon Nanofiber Cathode,” Chem. Mater., vol. 28, no. 3, pp. 896–905, Feb. 2016.
[22] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
[23] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
[24] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[25] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
[26] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
[27] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
[28] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
[29] R. Benato et al., “Sodium nickel chloride battery technology for large-scale stationary storage in the high voltage network,” J. Power Sources, vol. 293, pp. 127–136, 2015.
[30] G. L. Soloveichik, “Battery Technologies for Large-Scale Stationary Energy Storage,” Annu. Rev. Chem. Biomol. Eng, vol. 2, pp. 503–27, 2011.

## 183 Na-NiCl2 Battery
Technology |  | Na-NiCl2 battery
year |  | 2015 | 2020 | 2030 | 2050 | 2020 | 2020 | 2050 | 2050 | Note | Ref
est |  | ctrl | ctrl | ctrl | ctrl | Lower | Upper | Lower | Upper | - | -
cat | par
Energy/technical data
| Form of energy stored | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity | Electricity
| Application | ctrl: System, power- and energy-intensive; ctrl: System, power- and energy-intensive; ctrl: System, power- and energy-intensive; ctrl: System, power- and energy-intensive
| Energy storage capacity for one unit [MWh] | 4.43 | 4.15 | 4.15 | 4.15 | 3.11 | 5.19 | 3.11 | 5.19 | A,B,P | [12]+[11]
| Output capacity for one unit [MW] | 1.13 | 1.2 | 1.2 | 1.2 | 0.9 | 1.5 | 0.9 | 1.5 | A,B,P | [12]+[11]
| Input capacity for one unit [MW] | 0.42 | 0.45 | 0.45 | 0.45 | 0.34 | 0.56 | 0.34 | 0.56 | C,P | [34]+[8]
| Round trip efficiency DC [%] | 87 | 87 | 87 | 87 | 81 | 93 | 83 | 95 | D | [4]+[7]; [31]
- Charge efficiency [%] | bar: ctrl to Upper
- Discharge efficiency [%] | bar: ctrl to Upper
| Energy losses during storage [%/day] | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 15 | E,P | [35]+[5];[31]
| Forced outage [%] | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | F,P | [8]
| Planned outage [weeks/year] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F,P | [8]
| Technical lifetime [years] | 15 | 17 | 23 | 23 | 9 | 25 | 12 | 33 |  | [28]+[8];[30]+[32]+[31]
| Construction time [years] | 0.5 | 0.5 | 0.5 | 0.5 | 0.2 | 2 | 0.2 | 2 | G,P | [11]
Regulation ability
| Response time from idle to full-rated discharge [sec] | 0.02 | 0.02 | 0.02 | 0.02 | 0.001 | 0.02 | 0.001 | 0.02 |  | [10]/[4]+[33]
| Response time from full-rated charge to full-rated discharge [sec] | 0.5 | 0.5 | 0.5 | 0.5 | 0.001 | 0.5 | 0.001 | 0.5 | H,P | [4]
Financial data
| Specific investment [M€/MWh] | 1.0634 | 0.44663 | 0.27648 | 0.24458 | 0.34029 | 0.5636 | 0.19141 | 0.31902 | I, J | [12]+[28]; [30]+[31]
| - energy component [M€/MWh] | 0.80818 | 0.27648 | 0.14888 | 0.11697 | 0.22331 | 0.34029 | 0.095706 | 0.14888 | K | [12]; [31]
| - capacity component [M€/MW] | 0.51043 | 0.43599 | 0.35092 | 0.35092 | 0.31902 | 0.61677 | 0.26585 | 0.4998 | L | [12]; [31]
| - other project costs [M€/MWh] | 0.085072 | 0.031902 | 0.021268 | 0.021268 | 0.031902 | 0.042536 | 0.010634 | 0.021268 | 0 | [12]
| Fixed O&M [% total investment] | 1.5 | 1.5 | 1.5 | 1.5 | 0.9 | 2 | 0.9 | 2 | M | [29]+[28]+[27]
| Variable O&M [€/MWh] | 0.63804 | 0.63804 | 0.63804 | 0.63804 | 0.42536 | 2.2331 | 0.42536 | 2.2331 | N | [29]
Technology-specific data
| Alternative Investment cost [M€/MW] | 3.1902 | 1.4888 | 0.95706 | 0.85072 | 1.1697 | 1.9141 | 0.63804 | 1.0634 | I | [12]+[28]
| Lifetime in total number of cycles | 4500 | 4500 | 4500 | 4500 | 1500 | 11300 | 1500 | 11300 | O | [4]+[8];[30]+[32]
| Specific power [W/kg] | 16 | 16 | 16 | 16 | 12 | 20 | 12 | 20 | O,P | [8]
| Power density [W/m3] | 9350 | 9350 | 9350 | 9350 | 7012 | 11687 | 7012 | 11687 | O,P | [8]
| Specific energy [Wh/kg] | 56 | 56 | 56 | 56 | 42 | 70 | 42 | 70 | O,P | [3]
| Energy density [Wh/m3] | 32700 | 32700 | 32700 | 32700 | 24525 | 40875 | 24525 | 40875 | O,P | [3]
Notes
A. Italian batteries (Codrongianos (Sardinia) and Ciminna (Sicily)) used as standard.
B. Highly modular technology type with near linear scaling between total cost and installation size. Power and storage capacity cannot be varied independently.
C. Can fast recharge with rate identical to discharge rate. Standard charge/discharge time is 8/3 h.
D. Efficiency varies depending on use. Loss due to balance of system is approximately 2 % higher than for Li-ion batteries with similar PCS equipment [7]
E. During intended continuous operation, Ohmic losses maintain the temperature of the battery. Losses are thus included in round trip efficiency. No electrical self-discharge. Heat losses during idle periods on the order of 0.5 %/h discussed above. IRENA finds self-dischage/day to vary between 0.1 % and 15 % depending on unit and use [31]
F. Highly reliable and with no downtime required for maintenance during lifetime according to manufacturer.
G. Can be down to 2 months.
H. Measurement. Possibly limited by PCS.
I. For 2015, the specific storage to power capacity ratio is set to the average value for Italian “Terna Storage Lab” batteries. For future installations, the 4150 kWh and 1200 kW system is assumed.
J. Development rates from IRENA are used for prediction of future cost [30]
K. Includes “Batteries” from reference [12]
L. Includes “PCS-SCI”, “Transformer”, “Auxiliary equipment”, “Switching and actuating equipment”, and “System Controls & Instrumentation (SCI)” from reference [12].
M. Assumed similar to Na-S batteries in good agreement with data from EPRI [28]
N. Highly uncertain. Average value given. Reported in range 0.38 to 2.1 [29]
O. Data for Energy Spring 164 system from FZSoNick. Irena do not expected improvements on cell level. Improvements on installation level might occur [32]
P. Uncertainties are based on a qualified guess.
References
[1] J. L. Sudworth and R. C. Galloway, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS ¦ Sodium–Nickel Chloride,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 312–323.
[2] Z. Yang et al., “Electrochemical Energy Storage for Green Grid,” Chem. Rev., vol. 111, no. 5, pp. 3577–3613, May 2011.
[3] X. Lu, G. Li, J. Y. Kim, J. P. Lemmon, V. L. Sprenkle, and Z. Yang, “A novel low-cost sodium–zinc chloride battery,” Energy Environ. Sci., vol. 6, no. 6, p. 1837, 2013.
[4] R. Benato et al., “Sodium nickel chloride battery technology for large-scale stationary storage in the high voltage network,” J. Power Sources, vol. 293, pp. 127–136, 2015.
[5] G. L. Soloveichik, “Battery Technologies for Large-Scale Stationary Energy Storage,” Annu. Rev. Chem. Biomol. Eng, vol. 2, pp. 503–27, 2011.
[6] B. Parkhideh, “Project : Storage Technologies for Hybrid Electric Buses - Subject : ZEBRA Battery,” 2006.
[7] M. Pietrucci, “Progetti Pilota Power Intensive: Descrizione degli impianti e delle tecnologie,” 2017.
[8] FZSoNick, “DATASHEETS,” 2017. [Online]. Available: http://www.fzsonick.com/en/emea/energy-storage/prodotti/spring,-mod-164,-324.aspx.
[9] M. Hosseinifar and A. Petric, “Effect of High Charge Rate on Cycle Life of ZEBRA (Na/NiCl 2 ) Cells,” J. Electrochem. Soc., vol. 163, no. 7, pp. A1226–A1231, 2016.
[10] T. V Rachel Carnegie Douglas Gotham David Nderitu Paul Preckel, “Utility Scale Energy Storage Systems,” 2013.
“DOE Global Energy Storage Database.” [Online]. Available: https://www.energystorageexchange.org/. [Accessed: 29-Mar-2017].
[12] R. Benato, G. Bruno, F. Palone, R. Polito, and M. Rebolini, “Large-Scale Electrochemical Energy Storage in High Voltage Grids: Overview of the Italian Experience,” Energies, vol. 10, no. 1, p. 108, Jan. 2017.
[13] NGK Insulators LTD, “Case Studies.” pp. 1–13, 2016.
[14] NGK Insulators LTD, “The World’s Largest NAS Battery Installation Commences Operation Short Installation Period Achieved through Containerized, Compact Format,” 2016. [Online]. Available: http://www.ngk.co.jp/english/news/2016/0303.html.
[15] M. Andriollo et al., “Energy intensive electrochemical storage in Italy: 34.8 MW sodium-sulphur secondary cells,” J. Energy Storage, vol. 5, pp. 146–155, Feb. 2016.
[16] NGK Insulators LTD, “Structure of NAS Energy Storage System,” 2016. [Online]. Available: https://www.ngk.co.jp/nas/specs/.
[17] K. Bradbury, “Energy Storage Technology Review,” A Br. Introd. to Batter., no. September, pp. 1–33, 2010.
[18] IEC, “Electrical Energy Storage,” 2011.
[19] A. Colthorpe, “NGK’s NAS sodium sulfur grid-scale batteries in depth E,” Energy Storage News, 2017.
[20] C.-H. Dustmann and A. Bito, “SECONDARY BATTERIES – HIGH TEMPERATURE SYSTEMS ¦ Safety,” in Encyclopedia of Electrochemical Power Sources, 2009, pp. 324–333.
[21] R. C. Galloway, -Mes-Dea Sa, and C.-H. Dustmann, “ZEBRA Battery -Material Cost Availability and Recycling,” vol. 1519, 2003.
[22] H.-J. Chang, N. L. Canfield, K. Jung, V. L. Sprenkle, and G. Li, “Advanced Na-NiCl 2 Battery Using Nickel-Coated Graphite with Core− Shell Microarchitecture.”
[23] Fred Lambert, “Breakdown of raw materials in Tesla’s batteries and possible bottlenecks ¦ Electrek,” Electrek, 2016. [Online]. Available: https://electrek.co/2016/11/01/breakdown-raw-materials-tesla-batteries-possible-bottleneck/. [Accessed: 12-Sep-2017].
[24] S. Longo, V. Antonucci, M. Cellura, and M. Ferraro, “Life cycle assessment of storage systems: the case study of a sodium/nickel chloride battery,” J. Clean. Prod., vol. 85, pp. 337–346, 2014.
[25] O. Teller et al., “Joint EASE/EERA Recommendations for a European Energy Storage Technology Development Roadmap Towards 2030,” 2013.
[26] X. Lu et al., “Liquid-metal electrode to enable ultra-low temperature sodium–beta alumina batteries for renewable energy storage,” Nat. Commun., vol. 5, pp. 5884–5901, Aug. 2014.
[27] J. E. Al Carlsson, “ETRI 2014 - Energy Technology Reference Indicator projections for 2010-2050,” 2014.
[28] G. Huff et al., “DOE/EPRI 2013 electricity storage handbook in collaboration with NRECA,” Rep. SAND2013- …, no. July, p. 340, 2013.
[29] B. Zakeri and S. Syri, “Electrical energy storage systems: A comparative life cycle cost analysis,” Renew. Sustain. Energy Rev., vol. 42, pp. 569–596, 2015.
[30] K.-P. Kairies, “Battery storage technology improvements and cost reductions to 2030: A Deep Dive,” Int. Renew. Energy Agency Work., 2017.
[31] IRENA, “Electricity storage and renewables: Costs and markets to 2030 - Cost-of-service tool. Version 1.0,” 2017.
[32] P. Ralon, M. Taylor, and A. Ilas, Electricity storage and renewables: costs and market to 2030, no. October. 2017.
[33] L. Sigrist and E. Peirano, “E-Highway2050: Battery Storage Technology Assessment,” in WP3 workshop April 15th, 2014.
[34] J. Garche and C. K. Dyer, Encyclopedia of electrochemical power sources. Academic Press, 2009.
[35] H. Chen, T. N. Cong, W. Yang, C. Tan, Y. Li, and Y. Ding, “Progress in electrical energy storage system: A critical review,” Prog. Nat. Sci., vol. 19, no. 3, pp. 291–312, 2009.